## CELLS
Notes: 1. Values in "Time" column cannot be used to calculate "Actual Lime Rate" value. Actual Lime Rate (mg/L) value is independent of time as totalized values are read simultaneously. 2. Values in "Time" column reflects actual time LAO operator reads totalized values on Influent flow meters and lime-delivery system - Post 4-17-09. 3. While Lime Delivery System is operated in volumetric/manual settings, lime usage data is not measured or logged. | [24 empty] | Do Not Delete!
Do Not Move, Add, or Remove any Columns After "Date" without Updating the Column Name Definitions - Do Not Remove the "Count" that the Definitions Reference --> | [24 empty] | Count Chart Cells | 182
Date | Time | Lime Rate Set Point PRE (mg/L) | pH_INDC_PRE_(SU) | Lime Rate Set Point POST (mg/L) | pH INDC POST (SU) | Total Lime Used From Feeder Display (kg) | Actual Lime Rate (mg/L) | HCC-02A Total (gal) | Calc Totalizer: HCC-02A Flow (gpm) | HCC-02B Total (gal) | Calc Totalizer: HCC-02B Flow (gpm) | Main Influent Total (gallons) | Calculated Influent Flow Rate (gpm) | Calculated Totalizer: Total Influent Flow Rate (gpm) | Total Instant Influent Flow Rate (gpm) | Main Effluent Total (gallons) | Calculated Effluent Flow Rate (gpm) | Instant Flow OUT (gpm) | D4 Elevation(ft) (NGVD 29) | D4 Elevation(ft) (NAVD 88) | A2 (pH) | A3 (pH) | B2 (pH) | B3 (pH) | C2 (pH) | C3 (pH) | CT_EFS7(pH) | CT_IN04(pH) | Comments | pH Std High | Column1
2020-12-31 | 7:20 | 115 | 10.12 |  |  | 2126656 | #VALUE! |  |  |  |  | 1571464125 | #VALUE! |  | 1014 | 3740715750 | #VALUE! | 846 | 5413.69 | 5418.05 | 9.43 | 9.52 | ICE | 9.68 | ICE | 9.53 | 9.44 | 7.34 |  | 9.5 | No
2021-01-01 | 7:40 | 115 | 10.08 |  |  | 2127295 | 115.5539 |  |  |  |  | 1572925125 | 1000.6849 |  | 993 | 3741985750 | 869.863 | 842 | 5413.7 | 5418.06 | 9.36 | 9.5 | ICE | 9.63 | ICE | 9.49 | 9.42 | 7.39 |  | 9.5 | No
2021-01-02 | 7:10 | 115 | 10.07 |  |  | 2127914 | 115.0173 |  |  |  |  | 1574347000 | 1008.422 |  | 1021 | 3743217750 | 873.7589 | 831 | 5413.7 | 5418.06 | 9.44 | 9.39 | ICE | 9.5 | ICE | 9.38 | 9.32 | 7.55 |  | 9.5 | No
2021-01-03 | 9:00 | 115 | 10.01 |  |  | 2128600 | 115.413 |  |  |  |  | 1575917375 | 1013.1452 |  | 1018 | 3744578500 | 877.9032 | 862 | 5413.7 | 5418.06 | 9.46 | 9.43 | ICE | 9.46 | ICE | 9.39 | 9.32 | 7.64 |  | 9.5 | No
2021-01-04 | 10:30 | 115 | 10.08 |  |  | 2129267 | 115.1966 |  |  |  |  | 1577447125 | 999.8366 |  | 957 | 3745915000 | 873.5294 | 923 | 5413.71 | 5418.07 | 9.36 | 9.35 | ICE | 9.47 | ICE | 9.34 | 9.32 | 7.59 |  | 9.5 | No
2021-01-05 | 10:30 | 115 | 10.03 |  |  | 2129899 | 115.3142 |  |  |  |  | 1578895125 | 1005.5556 |  | 1050 | 3747191750 | 886.6319 | 874 | 5413.71 | 5418.07 | 9.36 | 9.39 | ICE | 9.49 | ICE | 9.35 | 9.3 | 7.52 |  | 9.5 | No
2021-01-06 | 9:10 | 115 | 9.98 |  |  | 2130484 | 115.4168 |  |  |  |  | 1580234250 | 984.6507 |  | 969 | 3748368500 | 865.2574 | 870 | 5413.73 | 5418.09 | 9.39 | 9.36 | ICE | 9.45 | ICE | 9.34 | 9.31 | 7.5 |  | 9.5 | No
2021-01-07 | 10:45 | 115 | 10.06 |  |  | 2131155 | 115.247 |  |  |  |  | 1581772500 | 1002.1173 |  | 1021 | 3749699250 | 866.9381 | 888 | 5413.7 | 5418.06 | 9.39 | 9.36 | ICE | 9.42 | ICE | 9.31 | 9.26 | 7.45 |  | 9.5 | No
2021-01-08 | 9:00 | 115 | 10.03 |  |  | 2131734 | 115.19 |  |  |  |  | 1583100500 | 994.7566 |  | 987 | 3750857750 | 867.7903 | 877 | 5413.72 | 5418.08 | 9.37 | 9.36 | ICE | 9.47 | ICE | 9.33 | 9.29 | 7.43 |  | 9.5 | No
2021-01-09 | 7:45 | 115 | 10.06 |  |  | 2132323 | 114.5275 |  |  |  |  | 1584459250 | 995.4212 |  | 1002 | 3752034000 | 861.7216 | 852 | 5413.69 | 5418.05 | 9.42 | 9.4 | ICE | 9.48 | ICE | 9.35 | 9.31 | 7.42 |  | 9.5 | No
2021-01-10 | 7:45 | 115 | 10.2 |  |  | 2132914 | 110.008 |  |  |  |  | 1585878625 | 985.6771 |  | 966 | 3753265000 | 854.8611 | 847 | 5413.7 | 5418.06 | 9.43 | 9.43 | ICE | 9.49 | ICE | 9.37 | 9.33 | 7.47 |  | 9.5 | No
2021-01-11 | 9:00 | 115 | 9.96 |  |  | 2133500 | 103.9072 |  |  |  |  | 1587368625 | 983.4983 |  | 1010 | 3754558000 | 853.4653 | 855 | 5413.69 | 5418.05 | 9.32 | 9.31 | ICE | 9.42 | ICE | 9.29 | 9.25 | 7.44 |  | 9.5 | No
2021-01-12 | 10:20 | 115 | 9.98 |  |  | 2134153 | 115.7 |  |  |  |  | 1588859750 | 981.0033 |  | 991 | 3755855750 | 853.7829 | 881 | 5413.69 | 5418.05 | 9.41 | 9.38 | ICE | 9.5 | ICE | 9.38 | 9.33 | 7.42 | Feeder ran in volumetric for aproximatley 25mins to tare/cal | 9.5 | No
2021-01-13 | 9:30 | 115 | 10.07 |  |  | 2134738 | 112.2931 |  |  |  |  | 1590236125 | 990.1978 |  | 925 | 3757052750 | 861.1511 | 852 | 5413.69 | 5418.05 | 9.37 | 9.36 | ICE | 9.46 | ICE | 9.33 | 9.3 | 7.42 |  | 9.5 | No
2021-01-14 | 9:40 | 115 | 9.99 |  |  | 2135376 | 119.9609 |  |  |  |  | 1591641250 | 969.0517 |  | 927 | 3758254500 | 828.7931 | 825 | 5413.71 | 5418.07 | 9.42 | 9.4 | ICE | 9.51 | ICE | 9.36 | 9.31 | 7.46 |  | 9.5 | No
2021-01-15 | 9:00 | 115 | 9.9 |  |  | 2135963 | 115.5094 |  |  |  |  | 1592983875 | 959.0179 |  | 966 | 3759408250 | 824.1071 | 828 | 5413.7 | 5418.06 | 9.42 | 9.36 | ICE | 9.46 | ICE | 9.34 | 9.29 | 7.46 |  | 9.5 | No
2021-01-16 | 7:45 | 115 | 9.96 |  |  | 2136553 | 115.316 |  |  |  |  | 1594335625 | 990.293 |  | 994 | 3760582500 | 860.2564 | 818 | 5413.7 | 5418.06 | 9.32 | 9.35 | ICE | 9.46 | ICE | 9.36 | 9.3 | 7.5 |  | 9.5 | No
2021-01-17 | 7:35 | 115 | 9.99 |  |  | 2137163 | 115.2601 |  |  |  |  | 1595733875 | 977.7972 |  | 970 | 3761793000 | 846.5035 | 854 | 5413.7 | 5418.06 | 9.29 | 9.32 | ICE | 9.43 | ICE | 9.33 | 9.29 | 7.55 |  | 9.5 | No
2021-01-18 | 8:35 | 115 | 10.04 |  |  | 2137803 | 114.7627 |  |  |  |  | 1597207250 | 982.25 |  | 989 | 3763076000 | 855.3333 | 845 | 5413.7 | 5418.06 | 9.4 | 9.41 | ICE | 9.49 | ICE | 9.36 | 9.31 | 7.44 |  | 9.5 | No
2021-01-19 | 7:45 | 115 | 10.02 |  |  | 2138392 | 115.3019 |  |  |  |  | 1598556875 | 970.9532 |  | 936 | 3764248250 | 843.3453 | 844 | 5413.7 | 5418.06 | 9.37 | 9.34 | ICE | 9.45 | ICE | 9.31 | 9.29 | 7.41 |  | 9.5 | No
2021-01-20 | 9:05 | 115 | 9.98 |  |  | 2139039 | 115.2067 |  |  |  |  | 1600040625 | 976.1513 |  | 993 | 3765515500 | 833.7171 | 851 | 5413.69 | 5418.05 | 9.32 | 9.3 | ICE | 9.44 | ICE | 9.3 | 9.25 | 7.53 |  | 9.5 | No
2021-01-21 | 10:30 | 115 | 10 |  |  | 2139690 | 115.2297 |  |  |  |  | 1601533250 | 978.7705 |  | 937 | 3766811500 | 849.8361 | 848 | 5413.72 | 5418.08 | 9.37 | 9.35 | ICE | 9.49 | ICE | 9.38 | 9.32 | 7.52 |  | 9.5 | No
2021-01-22 | 9:30 | 115 | 9.98 |  |  | 2140279 | 115.6231 |  |  |  |  | 1602879125 | 975.2717 |  | 1022 | 3767989500 | 853.6232 | 863 | 5413.69 | 5418.05 | 9.41 | 9.41 | ICE | 9.48 | ICE | 9.38 | 9.33 | 7.43 |  | 9.5 | No
2021-01-23 | 9:30 | 115 | 9.99 |  |  | 2140898 | 114.9567 |  |  |  |  | 1604301750 | 987.934 |  | 978 | 3769229000 | 860.7639 | 851 | 5413.69 | 5418.05 | 9.49 | 9.43 | ICE | 9.5 | ICE | 9.38 | 9.32 | 7.4 |  | 9.5 | No
2021-01-24 | 14:00 | 115 | 9.92 |  |  | 2141527 | 100.2079 |  |  |  |  | 1605960125 | 969.8099 |  | 1052 | 3770656000 | 834.5029 | 852 | 5413.69 | 5418.05 | 9.47 | 9.4 | ICE | 9.5 | ICE | 9.41 | 9.35 | 7.45 | Feeder ran in volumetric for aproximatley 3 hours due to silo knife gate stuck open | 9.5 | No
2021-01-25 | 11:30 | 115 | 9.96 |  |  | 2142067 | 113.7367 |  |  |  |  | 1607214500 | 972.3837 |  | 947 | 3771747250 | 845.9302 | 848 | 5413.69 | 5418.05 | 9.37 | 9.34 | ICE | 9.5 | ICE | 9.39 | 9.34 | 7.4 |  | 9.5 | No
2021-01-26 | 10:15 | 115 | 10.17 |  |  | 2142600 | 107.9383 |  |  |  |  | 1608519125 | 955.7692 |  | 949 | 3772872750 | 824.5421 | 457 | 5413.69 | 5418.05 | 9.38 | 9.35 | ICE | 9.54 | ICE | 9.44 | 9.29 | 7.52 | Feeder ran in volumetric for aproximatley 3 hours due to silo knife gate stuck open | 9.5 | No
2021-01-27 | 9:30 | 115 | 10.09 |  |  | 2143096 | 98.8449 |  |  |  |  | 1609844875 | 950.3584 |  | 947 | 3774225250 | 969.5341 | 829 | 5413.71 | 5418.07 | 9.44 | 9.41 | ICE | 9.58 | ICE | 9.45 | 9.4 | 7.52 |  | 9.5 | No
2021-01-28 | 8:30 | 115 | 9.98 |  |  | 2143669 | 115.3425 |  |  |  |  | 1611157375 | 951.087 |  | 975 | 3775392500 | 845.8333 | 821 | 5413.69 | 5418.05 | 9.41 | 9.38 | ICE | 9.57 | ICE | 9.46 | 9.27 | 7.38 |  | 9.5 | No
2021-01-29 | 9:00 | 115 | 9.79 |  |  | 2144249 | 115.1072 |  |  |  |  | 1612488625 | 905.6122 |  | 916 | 3776574500 | 804.0816 | 790 | 5413.6 | 5417.96 | 9.47 | 9.45 | ICE | 9.59 | ICE | 9.48 | 9.27 | 7.47 |  | 9.5 | No
2021-01-30 | 8:40 | 115 | 10.06 |  |  | 2144948 | 115.1169 |  |  |  |  | 1614092875 | 1129.7535 |  | 1009 | 3777908000 | 939.0845 | 985 | 5413.73 | 5418.09 | 9.41 | 9.45 | ICE | 9.52 | ICE | 9.4 | 9.28 | 7.41 |  | 9.5 | No
2021-01-31 | 9:20 | 115 | 10.07 |  |  | 2145626 | 115.5852 |  |  |  |  | 1615642625 | 1047.1284 |  | 1012 | 3779305750 | 944.4257 | 909 | 5413.7 | 5418.06 | 9.48 | 9.49 | ICE | 9.53 | ICE | 9.45 | 9.31 | 7.47 |  | 9.5 | No
2021-02-01 | 10:00 | 115 | 10.03 |  |  | 2146276 | 114.6973 |  |  |  |  | 1617139875 | 1011.6554 |  | 974 | 3780630750 | 895.2703 | 879 | 5413.73 | 5418.09 | 9.44 | 9.47 | ICE | 9.48 | ICE | 9.34 | 9.2 | 7.45 |  | 9.5 | No
2021-02-02 | 10:00 | 115 | 9.99 |  |  | 2146913 | 115.2909 |  |  |  |  | 1618599625 | 1013.7153 |  | 1034 | 3781915000 | 891.8403 | 897 | 5413.71 | 5418.07 | 9.35 | 9.43 | ICE | 9.46 | ICE | 9.38 | 9.24 | 7.43 |  | 9.5 | No
2021-02-03 | 9:25 | 115 | 9.98 |  |  | 2147557 | 115.2161 |  |  |  |  | 1620076375 | 1051.0676 |  | 1019 | 3783227750 | 934.3416 | 954 | 5413.68 | 5418.04 | 9.42 | 9.42 | ICE | 9.47 | ICE | 9.33 | 9.22 | 7.42 |  | 9.5 | No
2021-02-04 | 9:05 | 115 | 10.01 |  |  | 2148203 | 115.2033 |  |  |  |  | 1621557875 | 1043.3099 |  | 969 | 3784554000 | 933.9789 | 920 | 5413.69 | 5418.05 | 9.38 | 9.41 | ICE | 9.51 | ICE | 9.4 | 9.25 | 7.35 |  | 9.5 | No
2021-02-05 | 9:40 | 115 | 10.1 |  |  | 2148861 | 115.2621 |  |  |  |  | 1623066125 | 1022.5424 |  | 1069 | 3785892750 | 907.6271 | 923 | 5413.69 | 5418.05 | 9.4 | 9.51 | ICE | 9.55 | ICE | 9.46 | 9.31 | 7.44 |  | 9.5 | No
2021-02-06 | 7:20 | 115 | 10.03 |  |  | 2149444 | 115.2912 |  |  |  |  | 1624402125 | 1027.6923 |  | 1001 | 3787068000 | 904.0385 | 897 | 5413.73 | 5418.09 | 9.37 | 9.35 | ICE | 9.5 | ICE | 9.43 | 9.29 | 7.41 |  | 9.5 | No
2021-02-07 | 8:00 | 115 | 10.08 |  |  | 2150124 | 115.1644 |  |  |  |  | 1625962125 | 1054.0541 |  | 1060 | 3788456000 | 937.8378 | 1029 | 5413.72 | 5418.08 | 9.32 | 9.32 | ICE | 9.52 | ICE | 9.44 | 9.35 | 7.49 |  | 9.5 | No
2021-02-08 | 10:25 | 115 | 10.05 |  |  | 2150836 | 114.991 |  |  |  |  | 1627598000 | 1032.0978 |  | 1029 | 3789993250 | 969.8738 | 930 | 5413.71 | 5418.07 | 9.35 | 9.32 | ICE | 9.52 | ICE | 9.33 | 9.2 | 7.35 |  | 9.5 | No
2021-02-09 | 10:30 | 115 | 10.07 |  |  | 2151461 | 112.4929 |  |  |  |  | 1629065875 | 1015.8304 |  | 992 | 3791315750 | 915.2249 | 884 | 5413.72 | 5418.08 | 9.32 | 9.44 | ICE | 9.52 | ICE | 9.44 | 9.27 | 7.43 |  | 9.5 | No
2021-02-10 | 9:30 | 115 | 10.05 |  |  | 2152027 | 108.2821 |  |  |  |  | 1630446875 | 1000.7246 |  | 935 | 3792526500 | 877.3551 | 881 | 5413.72 | 5418.08 | 9.4 | 9.36 | ICE | 9.51 | ICE | 9.36 | 9.2 | 7.34 | Lime silo knife gate stuck open for aproximatley 15min | 9.5 | No
2021-02-11 | 11:00 | 115 | 10.04 |  |  | 2152663 | 109.6634 |  |  |  |  | 1631979125 | 1001.4706 |  | 959 | 3793884750 | 887.7451 | 894 | 5413.71 | 5418.07 | 9.41 | 9.4 | ICE | 9.54 | ICE | 9.39 | 9.26 | 7.38 |  | 9.5 | No
2021-02-12 | 9:00 | 115 | 10.12 |  |  | 2153155 | 97.3866 |  |  |  |  | 1633313875 | 1011.1742 |  | 1009 | 3795057250 | 888.2576 | 877 | 5413.69 | 5418.05 | 9.46 | 9.42 | ICE | 9.59 | ICE | 9.45 | 9.34 | 7.45 | Lime silo knife gate stuck open for aproximatley 15min | 9.5 | No
2021-02-13 | 8:55 | 115 | 10.29 |  |  | 2153689 | 97.6523 |  |  |  |  | 1634758625 | 1006.7944 |  | 1032 | 3796340250 | 894.0767 | 889 | 5413.71 | 5418.07 | 9.43 | 9.42 | ICE | 9.62 | ICE | 9.46 | 9.32 | 7.42 | Lime silo knife gate stuck open for aproximatley 15min | 9.5 | No
2021-02-14 | 9:40 | 115 | 9.98 |  |  | 2153925 | 42.3403 |  |  |  |  | 1636231250 | 991.6667 |  | 1011 | 3797657000 | 886.7003 | 866 | 5413.73 | 5418.09 | 9.46 | 9.49 | ICE | 9.67 | ICE | 9.58 | 9.38 | 7.38 | Upon arrival operator observed lime feeder/screw conveyor/slurry mixer were OFF for aproximatley 12hrs due to complications with HMI/WIN 911 systems. Operated in voulmetric for a portion of this time. | 9.5 | No
2021-02-15 | 11:50 | 115 | 10.09 |  |  | 2154544 | 103.5639 |  |  |  |  | 1637810375 | 1005.8121 |  | 943 | 3799037000 | 878.9809 | 884 | 5413.69 | 5418.05 | 9.52 | 9.48 | ICE | 9.55 | ICE | 9.43 | 9.33 | 7.4 |  | 9.5 | No
2021-02-16 | 12:35 | 115 | 10.05 |  |  | 2155174 | 111.5033 |  |  |  |  | 1639303125 | 1005.2189 |  | 941 | 3800358250 | 889.7306 | 890 | 5413.7 | 5418.06 | 9.52 | 9.51 | ICE | 9.52 | ICE | 9.45 | 9.39 | 7.5 |  | 9.5 | No
2021-02-17 | 8:40 | 115 | 10.03 |  |  | 2155691 | 115.1459 |  |  |  |  | 1640489375 | 984.4398 |  | 953 | 3801417500 | 879.0456 | 868 | 5413.71 | 5418.07 | 9.45 | 9.44 | ICE | 9.47 | ICE | 9.38 | 9.28 | 7.43 |  | 9.5 | No
2021-02-18 | 8:30 | 115 | 10.02 |  |  | 2156299 | 115.1396 |  |  |  |  | 1641884500 | 975.6119 |  | 1002 | 3802647250 | 859.965 | 853 | 5413.69 | 5418.05 | 9.42 | 9.41 | ICE | 9.44 | ICE | 9.37 | 9.24 | 7.4 |  | 9.5 | No
2021-02-19 | 9:00 | 115 | 10.05 |  |  | 2156929 | 115.2677 |  |  |  |  | 1643328500 | 982.3129 |  | 979 | 3803909250 | 858.5034 | 862 | 5413.71 | 5418.07 | 9.34 | 9.45 | ICE | 9.48 | ICE | 9.41 | 9.41 | 7.48 |  | 9.5 | No
2021-02-20 | 12:35 | 115 | 9.95 |  |  | 2157657 | 115.3279 |  |  |  |  | 1644996250 | 1007.7039 |  | 1011 | 3805375000 | 885.6495 | 895 | 5413.7 | 5418.06 | 9.45 | 9.41 | ICE | 9.46 | ICE | 9.4 | 9.38 | 7.52 |  | 9.5 | No
2021-02-21 | 8:45 | 115 | 10.01 |  |  | 2158183 | 114.9103 |  |  |  |  | 1646205625 | 999.4835 |  | 970 | 3806435500 | 876.4463 | 873 | 5413.71 | 5418.07 | 9.52 | 9.46 | ICE | 9.49 | ICE | 9.41 | 9.42 | 7.43 |  | 9.5 | No
2021-02-22 | 9:50 | 115 | 9.98 |  |  | 2158824 | 115.54 |  |  |  |  | 1647671375 | 973.9203 |  | 970 | 3807736000 | 864.1196 | 864 | 5413.72 | 5418.08 | 9.42 | 9.38 | ICE | 9.47 | ICE | 9.36 | 9.25 | 7.37 |  | 9.5 | No
2021-02-23 | 10:00 | 115 | 9.98 |  |  | 2159517 | 115.1426 |  |  |  |  | 1649261500 | 1096.6379 |  | 994 | 3809052000 | 907.5862 | 1000 | 5413.77 | 5418.13 | 9.41 | 9.42 | ICE | 9.49 | ICE | 9.43 | 9.37 | 7.53 |  | 9.5 | No
2021-02-24 | 9:05 | 115 | 9.96 |  |  | 2160150 | 115.4567 |  |  |  |  | 1650710000 | 1045.8484 |  | 1071 | 3810357750 | 942.7798 | 925 | 5413.7 | 5418.06 | 9.42 | 9.4 | ICE | 9.49 | ICE | 9.4 | 9.32 | 7.37 |  | 9.5 | No
2021-02-25 | 8:45 | 115 | 9.94 |  |  | 2160777 | 112.9202 |  |  |  |  | 1652177000 | 1033.0986 |  | 1084 | 3811640000 | 902.993 | 905 | 5413.7 | 5418.06 | 9.44 | 9.4 | ICE | 9.49 | ICE | 9.37 | 9.31 | 7.34 |  | 9.5 | No
2021-02-26 | 7:50 | 115 | 10.06 |  |  | 2161382 | 113.9385 |  |  |  |  | 1653579875 | 1012.9061 |  | 1024 | 3812893250 | 904.8736 | 899 | 5413.7 | 5418.06 | 9.42 | 9.42 | ICE | 9.55 | ICE | 9.49 | 9.41 | 7.39 |  | 9.5 | No
2021-02-27 | 7:45 | 115 | 9.98 |  |  | 2162012 | 115.638 |  |  |  |  | 1655019250 | 1003.0488 |  | 966 | 3814168250 | 888.5017 | 862 | 5413.71 | 5418.07 | 9.46 | 9.43 | ICE | 9.5 | ICE | 9.42 | 9.32 | 7.48 |  | 9.5 | No
2021-02-28 | 7:30 | 115 | 10 |  |  | 2162604 | 111.045 |  |  |  |  | 1656427750 | 988.4211 |  | 938 | 3815415000 | 874.9123 | 854 | 5413.7 | 5418.06 | 9.43 | 9.4 | ICE | 9.57 | ICE | 9.48 | 9.38 | 7.55 |  | 9.5 | No
2021-03-01 | 8:05 | 115 | 10.03 |  |  | 2163233 | 114.1656 |  |  |  |  | 1657883375 | 986.8644 |  | 999 | 3816705500 | 874.9153 | 847 | 5413.7 | 5418.06 | 9.46 | 9.43 | ICE | 9.49 | ICE | 9.44 | 9.34 | 7.42 |  | 9.5 | No
2021-03-02 | 9:10 | 115 | 10.01 |  |  | 2163911 | 115.4269 |  |  |  |  | 1659435250 | 1031.1462 |  | 1069 | 3818038250 | 885.5482 | 922 | 5413.71 | 5418.07 | 9.44 | 9.42 | ICE | 9.5 | ICE | 9.43 | 9.36 | 7.42 |  | 9.5 | No
2021-03-03 | 8:30 | 115 | 9.98 |  |  | 2164566 | 115.5506 |  |  |  |  | 1660932875 | 1069.7321 |  | 965 | 3819330000 | 922.6786 | 928 | 5413.73 | 5418.09 | 9.42 | 9.39 | ICE | 9.47 | ICE | 9.38 | 9.31 | 7.34 |  | 9.5 | No
2021-03-04 | 8:25 | 115 | 9.96 |  |  | 2165272 | 114.6969 |  |  |  |  | 1662559125 | 1133.2753 |  | 1077 | 3820732500 | 977.3519 | 991 | 5413.73 | 5418.09 | 9.32 | 9.31 | ICE | 9.39 | ICE | 9.29 | 9.25 | 7.36 |  | 9.5 | No
2021-03-05 | 9:50 | 115 | 9.98 |  |  | 2166014 | 114.8766 |  |  |  |  | 1664265625 | 1119.0164 |  | 1016 | 3822215500 | 972.459 | 1046 | 5414.76 | 5419.12 | 9.4 | 9.4 | ICE | 9.47 | ICE | 9.39 | 9.32 | 7.37 |  | 9.5 | No
2021-03-06 | 8:25 | 115 | 9.99 |  |  | 2166754 | 115.2253 |  |  |  |  | 1665962375 | 1252.214 |  | 1010 | 3823706250 | 1100.1845 | 1086 | 5413.77 | 5418.13 | 9.37 | 9.4 | ICE | 9.48 | ICE | 9.44 | 9.33 | 7.33 |  | 9.5 | No
2021-03-07 | 8:40 | 115 | 10.1 |  |  | 2167509 | 115.3348 |  |  |  |  | 1667691875 | 1188.6598 |  | 1009 | 3825256000 | 1065.1203 | 1072 | 5413.77 | 5418.13 | 9.42 | 9.43 | ICE | 9.54 | ICE | 9.47 | 9.23 | 7.39 |  | 9.5 | No
2021-03-08 | 9:25 | 115 | 10.07 |  |  | 2168305 | 115.0537 |  |  |  |  | 1669519750 | 1230.8923 |  | 1027 | 3826859500 | 1079.798 | 1115 | 5413.79 | 5418.15 | 9.45 | 9.42 | ICE | 9.54 | ICE | 9.49 | 9.35 | 7.36 | C1 Free of ice | 9.5 | No
2021-03-09 | 10:20 | 115 | 10.07 |  |  | 2169068 | 115.4224 |  |  |  |  | 1671266250 | 1168.2274 |  | 1132 | 3828473750 | 1079.7659 | 1041 | 5413.75 | 5418.11 | 9.49 | 9.46 | ICE | 9.62 | ICE | 9.55 | 9.4 | 7.36 |  | 9.5 | No
2021-03-10 | 7:30 | 115 | 9.99 |  |  | 2169766 | 115.024 |  |  |  |  | 1672869500 | 1262.4016 |  | 1258 | 3829847250 | 1081.4961 | 1112 | 5413.77 | 5418.13 | 9.34 | 9.34 | ICE | 9.48 | ICE | 9.43 | 9.31 | 7.38 |  | 9.5 | No
2021-03-11 | 9:05 | 115 | 9.96 |  |  | 2170571 | 115.103 |  |  |  |  | 1674717250 | 1203.7459 |  | 1077 | 3831530750 | 1096.7427 | 1064 | 5413.78 | 5418.14 | 9.39 | 9.36 | ICE | 9.49 | ICE | 9.37 | 9.29 | 7.34 |  | 9.5 | No
2021-03-12 | 8:30 | 115 | 10.11 |  |  | 2171294 | 115.5142 |  |  |  |  | 1676370875 | 1176.9573 |  | 939 | 3832983250 | 1033.8078 | 1010 | 5413.64 | 5418 | 9.52 | 9.51 | ICE | 9.54 | ICE | 9.45 | 9.39 | 7.44 |  | 9.5 | No
2021-03-13 | 9:30 | 115 | 10.77 |  |  | 2172022 | 115.4751 |  |  |  |  | 1678036500 | 1110.4167 |  | 1243 | 3834470500 | 991.5 | 1012 | 5413.64 | 5418 | 9.58 | 9.48 | ICE | 9.54 | ICE | 9.47 | 9.39 | 7.35 |  | 9.5 | No
2021-03-14 | 6:15 | 115 | 10.09 |  |  | 2172651 | 115.1246 |  |  |  |  | 1679480000 | 1159.4378 |  | 938 | 3835671250 | 964.4578 | 1094 | 5413.64 | 5418 | 9.53 | 9.53 | ICE | 9.58 | ICE | 9.53 | 9.4 | 7.4 |  | 9.5 | No
2021-03-15 | 9:20 | 115 | 9.97 |  |  | 2173508 | 115.0801 |  |  |  |  | 1681447500 | 1210.7692 |  | 997 | 3837417000 | 1074.3077 | 1136 | 5413.76 | 5418.12 | 9.43 | 9.44 | ICE | 9.51 | ICE | 9.4 | 9.36 | 7.34 | A1 and B1 thawed over the weekend | 9.5 | No
2021-03-16 | 10:30 | 115 | 10.1 |  |  | 2174320 | 115.3625 |  |  |  |  | 1683307125 | 1231.5397 |  | 943 | 3839079750 | 1101.1589 | 1120 | 5413.72 | 5418.08 | 9.49 | 9.47 | ICE | 9.53 | ICE | 9.48 | 9.36 | 7.33 |  | 9.5 | No
2021-03-17 | 9:25 | 115 | 10.04 |  |  | 2175072 | 114.9596 |  |  |  |  | 1685035375 | 1256.9091 |  | 929 | 3840593250 | 1100.7273 | 1108 | 5413.63 | 5417.99 | 9.38 | 9.37 | ICE | 9.48 | ICE | 9.39 | 9.28 | 7.3 |  | 9.5 | No
2021-03-18 | 9:00 | 115 | 10.07 |  |  | 2175804 | 115.52 |  |  |  |  | 1686709500 | 1183.1272 |  | 1207 | 3842125250 | 1082.6855 | 1084 | 5413.77 | 5418.13 | 9.45 | 9.42 | 9.47 | 9.48 | 9.43 | 9.43 | 9.3 | 7.38 | B2 and C2 free of ice | 9.5 | No
2021-03-19 | 9:00 | 115 | 10.15 |  |  | 2176581 | 115.4254 |  |  |  |  | 1688488000 | 1235.0694 |  | 1016 | 3843670250 | 1072.9167 | 1105 | 5413.74 | 5418.1 | 9.46 | 9.46 | 9.54 | 9.53 | 9.5 | 9.49 | 9.36 | 7.49 |  | 9.5 | No
2021-03-20 | 8:20 | 115 | 10.06 |  |  | 2177334 | 115.1708 |  |  |  |  | 1690215375 | 1233.8393 |  | 990 | 3845222500 | 1108.75 | 1098 | 5413.74 | 5418.1 | 9.44 | 9.48 | 9.56 | 9.52 | 9.51 | 9.48 | 9.37 | 7.44 | A2 thawed | 9.5 | No
2021-03-21 | 9:40 | 115 | 10.15 |  |  | 2178073 | 115.2309 |  |  |  |  | 1691909750 | 1114.7204 |  | 1009 | 3846795750 | 1035.0329 | 987 | 5413.73 | 5418.09 | 9.37 | 9.42 | 9.58 | 9.53 | 9.51 | 9.53 | 9.36 | 7.48 |  | 9.5 | No
2021-03-22 | 9:00 | 115 | 10.17 |  |  | 2178737 | 115.2434 |  |  |  |  | 1693432000 | 1087.3214 |  | 1026 | 3848142750 | 962.1429 | 948 | 54113.72 | 54118.08 | 9.36 | 9.42 | 9.57 | 9.58 | 9.51 | 9.48 | 9.34 | 7.43 |  | 9.5 | No
2021-03-23 | 10:20 | 115 | 10.07 |  |  | 2179456 | 115.3372 |  |  |  |  | 1695079000 | 1083.5526 |  | 1014 | 3849604000 | 961.3487 | 962 | 5413.7 | 5418.06 | 9.46 | 9.47 | 9.61 | 9.59 | 9.51 | 9.51 | 9.39 | 7.46 |  | 9.5 | No
2021-03-24 | 7:40 | 115 | 10.12 |  |  | 2180057 | 115.3854 |  |  |  |  | 1696455125 | 1075.0977 |  | 1059 | 3850814250 | 945.5078 | 936 | 5413.72 | 5418.08 | 9.48 | 9.43 | 9.51 | 9.5 | 9.43 | 9.41 | 9.29 | 7.41 |  | 9.5 | No
2021-03-25 | 9:05 | 115 | 10.03 |  |  | 2180782 | 115.3455 |  |  |  |  | 1698115750 | 1088.9344 |  | 1071 | 3852245250 | 938.3607 | 936 | 5413.74 | 5418.1 | 9.46 | 9.45 | 9.57 | 9.54 | 9.44 | 9.44 | 9.33 | 7.38 |  | 9.5 | No
2021-03-26 | 7:10 | 115 | 10.04 |  |  | 2181407 | 115.4018 |  |  |  |  | 1699546625 | 1079.9057 |  | 1104 | 3853477000 | 929.6226 | 940 | 5413.72 | 5418.08 | 9.53 | 9.49 | 9.59 | 9.57 | 9.47 | 9.46 | 9.36 | 7.42 |  | 9.5 | No
2021-03-27 | 8:00 | 115 | 10.13 |  |  | 2182094 | 114.5961 |  |  |  |  | 1701130500 | 1063.0034 |  | 1079 | 3854861500 | 929.1946 | 907 | 5413.73 | 5418.09 | 9.37 | 9.42 | 9.57 | 9.55 | 9.49 | 9.46 | 9.34 | 7.49 |  | 9.5 | No
2021-03-28 | 8:10 | 115 | 10.13 |  |  | 2182760 | 115.3632 |  |  |  |  | 1702655750 | 1051.8966 |  | 1114 | 3856183750 | 911.8966 | 929 | 5413.7 | 5418.06 | 9.38 | 9.39 | 9.57 | 9.5 | 9.43 | 9.43 | 9.31 | 7.46 |  | 9.5 | No
2021-03-29 | 9:45 | 115 | 10.2 |  |  | 2183475 | 114.8001 |  |  |  |  | 1704301250 | 1071.987 |  | 922 | 3857615750 | 932.899 | 948 | 5413.68 | 5418.04 | 9.34 | 9.39 | 9.52 | 9.48 | 9.41 | 9.36 | 9.28 | 7.54 |  | 9.5 | No
2021-03-30 | 10:45 | 115 | 10.15 |  |  | 2184150 | 115.1573 |  |  |  |  | 1705849875 | 1032.4167 |  | 1085 | 3859008500 | 928.5 | 919 | 5413.75 | 5418.11 | 9.36 | 9.37 | 9.6 | 9.52 | 9.52 | 9.39 | 9.232 | 7.51 |  | 9.5 | No
2021-03-31 | 8:00 | 115 | 10.01 |  |  | 2184726 | 115.3204 |  |  |  |  | 1707169500 | 1035 |  | 936 | 3860160500 | 903.5294 | 903 | 5413.8 | 5418.16 | 9.26 | 9.24 | 9.49 | 9.43 | 9.43 | 9.29 | 9.16 | 7.4 |  | 9.5 | No
2021-04-01 | 10:40 | 115 | 9.98 |  |  | 2185447 | 115.2121 |  |  |  |  | 1708822875 | 1033.3594 |  | 966 | 3861603500 | 901.875 | 912 | 5413.72 | 5418.08 | 9.18 | 9.16 | 9.4 | 9.38 | 9.29 | 9.27 | 9.16 | 7.35 | Feed rate increased to 120 mg/l @ 13:00 | 9.5 | No
2021-04-02 | 8:45 | 120 | 10.08 |  |  | 2186080 | 119.8202 |  |  |  |  | 1710218625 | 1053.3962 |  | 980 | 3862819250 | 917.5472 | 922 | 5413.72 | 5418.08 | 9.2 | 9.23 | 9.45 | 9.46 | 9.39 | 9.36 | 9.3 | 7.45 |  | 9.5 | No
2021-04-03 | 9:00 | 120 | 10.09 |  |  | 2186774 | 119.8891 |  |  |  |  | 1711748000 | 1051.1168 |  | 915 | 3864153250 | 916.8385 | 915 | 5413.72 | 5418.08 | 9.21 | 9.18 | 9.4 | 9.41 | 9.33 | 9.3 | 9.25 | 7.46 |  | 9.5 | No
2021-04-04 | 8:55 | 120 | 10.13 |  |  | 2187465 | 121.0528 |  |  |  |  | 1713256125 | 1050.9582 |  | 917 | 3865450500 | 904.007 | 917 | 5413.75 | 5418.11 | 9.25 | 9.2 | 9.42 | 9.4 | 9.35 | 9.26 | 9.23 | 7.45 |  | 9.5 | No
2021-04-05 | 10:20 | 120 | 10.19 |  |  | 2188214 | 119.9493 |  |  |  |  | 1714905875 | 1081.8033 |  | 1204 | 3866833750 | 907.0492 | 940 | 5413.72 | 5418.08 | 9.26 | 9.18 | 9.45 | 9.42 | 9.32 | 9.25 | 9.22 | 7.44 |  | 9.5 | No
2021-04-06 | 10:10 | 120 | 10.08 |  |  | 2188970 | 120.4044 |  |  |  |  | 1716564750 | 1160.0524 |  | 983 | 3868250750 | 990.9091 | 987 | 5413.71 | 5418.07 | 9.26 | 9.16 | 9.46 | 9.43 | 9.38 | 9.3 | 9.23 | 7.41 |  | 9.5 | No
2021-04-07 | 8:45 | 120 | 10.03 |  |  | 2189631 | 120.0871 |  |  |  |  | 1718019000 | 1073.2472 |  | 1096 | 3869545000 | 955.1661 | 936 | 5413.76 | 5418.12 | 9.24 | 9.14 | 9.41 | 9.38 | 9.3 | 9.29 | 9.2 | 7.39 |  | 9.5 | No
2021-04-08 | 6:55 | 120 | 10.03 |  |  | 2190283 | 120.2506 |  |  |  |  | 1719451500 | 1077.0677 |  | 1035 | 3870693500 | 863.5338 | 852 | 5413.73 | 5418.09 | 9.32 | 9.15 | 9.47 | 9.41 | 9.33 | 9.27 | 9.21 | 7.4 |  | 9.5 | No
2021-04-09 | 9:15 | 120 | 10.05 |  |  | 2191042 | 120.32 |  |  |  |  | 1721118125 | 1054.8259 |  | 1057 | 3871933750 | 784.9684 | 813 | 5413.72 | 5418.08 | 9.22 | 9.1 | 9.48 | 9.44 | 9.3 | 9.23 | 9.16 | 7.43 |  | 9.5 | No
2021-04-10 | 7:20 | 120 | 10.04 |  |  | 2191748 | 120.5726 |  |  |  |  | 1722665125 | 1167.5472 |  | 1368 | 3873127750 | 901.1321 | 975 | 5413.68 | 5418.04 | 9.28 | 9.12 | 9.52 | 9.48 | 9.39 | 9.32 | 9.23 | 7.44 |  | 9.5 | No
2021-04-11 | 7:15 | 120 | 10.05 |  |  | 2192456 | 120.1858 |  |  |  |  | 1724221500 | 1084.5819 |  | 1121 | 3874494500 | 952.439 | 916 | 5413.7 | 5418.06 | 9.29 | 9.14 | 9.51 | 9.49 | 9.39 | 9.34 | 9.19 | 7.44 |  | 9.5 | No
2021-04-12 | 11:20 | 120 | 10.23 |  |  | 2193267 | 119.9367 |  |  |  |  | 1726008000 | 1060.2374 |  | 979 | 3876025000 | 908.3086 | 886 | 5413.73 | 5418.09 | 9.29 | 9.16 | 9.55 | 9.54 | 9.48 | 9.42 | 9.24 | 7.46 |  | 9.5 | No
2021-04-13 | 8:45 | 120 | 10.22 |  |  | 2193885 | 120.4434 |  |  |  |  | 1727363625 | 1054.9611 |  | 1015 | 3877059000 | 804.6693 | 820 | 5413.69 | 5418.05 | 9.31 | 9.14 | 9.6 | 9.58 | 9.47 | 9.41 | 9.3 | 7.45 |  | 9.5 | No
2021-04-14 | 9:15 | 120 | 10.16 |  |  | 2194621 | 120.1061 |  |  |  |  | 1728982625 | 1101.3605 |  | 1083 | 3878248500 | 809.1837 | 869 | 5413.74 | 5418.1 | 9.32 | 9.12 | 9.59 | 9.55 | 9.42 | 9.36 | 9.25 | 7.48 |  | 9.5 | No
2021-04-15 | 8:20 | 120 | 10.23 |  |  | 2195369 | 120.3362 |  |  |  |  | 1730624875 | 1185.7401 |  | 961 | 3879433500 | 855.5957 | 919 | 5413.69 | 5418.05 | 9.34 | 9.15 | 9.6 | 9.58 | 9.45 | 9.39 | 9.26 | 7.45 | Switched to IPS pump #2 @10:45 now using IPS 3011 flow meter for lime feed signal | 9.5 | No
2021-04-16 | 9:15 | 120 | 10.25 |  |  | 2196157 | NA |  |  |  |  | 1771481375 | NA |  | 1143 | 3880785500 | 904.3478 | 926 | 5413.75 | 5418.11 | 9.35 | 9.15 | 9.53 | 9.53 | 9.43 | 9.39 | 9.27 | 7.3 |  | 9.5 | No
2021-04-17 | 10:00 | 120 | 10.27 |  |  | 2196832 | 121.1107 |  |  |  |  | 1772953875 | 991.5825 |  | 1061 | 3882197250 | 950.6734 | 947 | 5413.75 | 5418.11 | 9.21 | 9.09 | 9.53 | 9.53 | 9.42 | 9.38 | 9.29 | 7.45 |  | 9.5 | No
2021-04-18 | 9:05 | 120 | 10.24 |  |  | 2197529 | 120.2108 |  |  |  |  | 1774485750 | 1106.0469 |  | 986 | 3883454750 | 907.9422 | 892 | 5413.75 | 5418.11 | 9.16 | 9.1 | 9.47 | 9.5 | 9.4 | 9.38 | 9.3 | 7.44 |  | 9.5 | No
2021-04-19 | 9:15 | 120 | 9.91 |  |  | 2198120 | 128.1302 |  |  |  |  | 1775704375 | 840.431 |  | 1271 | 3884734500 | 882.5862 | 914 | 5413.79 | 5418.15 | 9.32 | 9.18 | 9.53 | 9.51 | 9.45 | 9.36 | 9.3 | 7.48 |  | 9.5 | No
2021-04-20 | 8:25 | 120 | 10.28 |  |  | 2198713 | NA |  |  |  |  | 1730836750 | NA |  | 1048 | 3885942500 | 869.0647 | 849 | 5413.74 | 5418.1 | 9.27 | 9.15 | 9.52 | 9.49 | 9.37 | 9.35 | 9.3 | 7.44 | Switched to IPS pump #1 @8:30 now using IPS 3005 flow meter for lime feed signal | 9.5 | No
2021-04-21 | 9:15 | 120 | 10.25 |  |  | 2199424 | 119.6571 |  |  |  |  | 1732406625 | 1053.6074 |  | 1042 | 3887104000 | 779.5302 | 825 | 5413.68 | 5418.04 | 9.26 | 9.17 | 9.46 | 9.48 | 9.37 | 9.36 | 9.31 | 7.42 |  | 9.5 | No
2021-04-22 | 8:30 | 120 | 10.2 |  |  | 2200170 | 120.796 |  |  |  |  | 1734038250 | 1169.6237 |  | 933 | 3888282500 | 844.8029 | 933 | 5413.68 | 5418.04 | 9.29 | 9.22 | 9.45 | 9.43 | 9.34 | 9.31 | 9.23 | 7.52 |  | 9.5 | No
2021-04-23 | 8:25 | 120 | 10.13 |  |  | 2200911 | 120.3275 |  |  |  |  | 1735665250 | 1133.7979 |  | 1094 | 3889566250 | 894.5993 | 937 | 5413.74 | 5418.1 | 9.25 | 9.16 | 9.42 | 9.37 | 9.3 | 9.21 | 9.18 | 7.43 |  | 9.5 | No
2021-04-24 | 8:10 | 120 | 10.1 |  |  | 2201657 | 120.4086 |  |  |  |  | 1737302125 | 1148.6842 |  | 1027 | 3890940750 | 964.5614 | 986 | 5413.71 | 5418.07 | 9.2 | 9.15 | 9.41 | 9.37 | 9.31 | 9.25 | 9.2 | 7.4 |  | 9.5 | No
2021-04-25 | 7:30 | 120 | 10.14 |  |  | 2202345 | 120.3676 |  |  |  |  | 1738812250 | 1078.6607 |  | 1092 | 3892271250 | 950.3571 | 922 | 5413.8 | 5418.16 | 9.23 | 9.15 | 9.46 | 9.39 | 9.34 | 9.28 | 9.22 | 7.38 |  | 9.5 | No
2021-04-26 | 10:10 | 120 | 10.06 |  |  | 2203135 | 120.3509 |  |  |  |  | 1740546500 | 1083.9063 |  | 1130 | 3893769000 | 936.0938 | 951 | 5413.7 | 5418.06 | 9.26 | 9.14 | 9.49 | 9.45 | 9.41 | 9.34 | 9.27 | 7.27 |  | 9.5 | No
2021-04-27 | 8:55 | 120 | 10.12 |  |  | 2203812 | 120.2245 |  |  |  |  | 1742034250 | 1089.9267 |  | 1121 | 3894924500 | 846.5201 | 860 | 5413.72 | 5418.08 | 9.24 | 9.13 | 9.44 | 9.44 | 9.38 | 9.33 | 9.27 | 7.38 |  | 9.5 | No
2021-04-28 | 8:55 | 120 | 10.14 |  |  | 2204541 | 120.3483 |  |  |  |  | 1743634625 | 1111.3715 |  | 1068 | 3896164750 | 861.2847 | 899 | 5413.73 | 5418.09 | 9.25 | 9.14 | 9.41 | 9.4 | 9.34 | 9.29 | 9.24 | 7.37 |  | 9.5 | No
2021-04-29 | 9:05 | 120 | 10.03 |  |  | 2205251 | 120.2934 |  |  |  |  | 1745194000 | 1075.431 |  | 985 | 3897335500 | 807.4138 | 820 | 5413.73 | 5418.09 | 9.23 | 9.13 | 9.45 | 9.39 | 9.28 | 9.25 | 9.18 | 7.37 |  | 9.5 | No
2021-04-30 | 10:15 | 120 | 10.15 |  |  | 2206018 | 119.9154 |  |  |  |  | 1746883875 | 1119.1225 |  | 1067 | 3898541750 | 798.8411 | 868 | 5413.78 | 5418.14 | 9.22 | 9.03 | 9.44 | 9.41 | 9.31 | 9.27 | 9.18 | 7.4 |  | 9.5 | No
2021-05-01 | 7:10 | 120 | 10.06 |  |  | 2206654 | 120.7775 |  |  |  |  | 1748275125 | 1108.5657 |  | 1177 | 3899641000 | 875.8964 | 904 | 5413.73 | 5418.09 | 9.24 | 9.06 | 9.48 | 9.43 | 9.36 | 9.28 | 9.21 | 7.39 |  | 9.5 | No
2021-05-02 | 7:00 | 120 | 10.1 |  |  | 2207399 | 120.1371 |  |  |  |  | 1749913500 | 1145.7168 |  | 976 | 3900983750 | 938.986 | 939 | 5413.7 | 5418.06 | 9.24 | 9.07 | 9.51 | 9.44 | 9.39 | 9.33 | 9.22 | 7.41 |  | 9.5 | No
2021-05-03 | 8:20 | 120 | 9.98 |  |  | 2208117 | 119.928 |  |  |  |  | 1751495250 | 1040.625 |  | 998 | 3902345500 | 895.8882 | 867 | 5413.7 | 5418.06 | 9.13 | 9.03 | 9.45 | 9.42 | 9.35 | 9.28 | 9.08 | 7.39 |  | 9.5 | No
2021-05-04 | 9:55 | 120 | 10.08 |  |  | 2208842 | 120.2043 |  |  |  |  | 1753088750 | 1038.1107 |  | 1088 | 3903545000 | 781.4332 | 804 | 5413.72 | 5418.08 | 9.12 | 9 | 9.46 | 9.45 | 9.37 | 9.31 | 9.21 | 7.43 | Feed rate increased to 125 mg/l @ 15:30 | 9.5 | No
2021-05-05 | 9:00 | 125 | 10.21 |  |  | 2209535 | 124.2138 |  |  |  |  | 1754562750 | 1064.2599 |  | 1084 | 3904632750 | 785.3791 | 824 | 5413.69 | 5418.05 | 9.18 | 9 | 9.48 | 9.44 | 9.34 | 9.3 | 9.2 | 7.44 |  | 9.5 | No
2021-05-06 | 9:15 | 125 | 10.07 |  |  | 2210278 | 125.5022 |  |  |  |  | 1756126875 | 1075 |  | 1119 | 3905817750 | 814.433 | 844 | 5413.71 | 5418.07 | 9.14 | 8.98 | 9.45 | 9.43 | 9.36 | 9.27 | 9.15 | 7.4 |  | 9.5 | No
2021-05-07 | 12:15 | 125 | 10.09 |  |  | 2211090 | 124.9999 |  |  |  |  | 1757843125 | 1059.4136 |  | 1160 | 3907202000 | 854.4753 | 851 | 5413.71 | 5418.07 | 9.23 | 8.96 | 9.44 | 9.44 | 9.38 | 9.28 | 9.16 | 7.44 |  | 9.5 | No
2021-05-08 | 11:15 | 125 | 10.23 |  |  | 2211821 | 125.1556 |  |  |  |  | 1759386250 | 1118.2065 |  | 1054 | 3908477250 | 924.0942 | 935 | 5413.74 | 5418.1 | 9.09 | 8.91 | 9.45 | 9.4 | 9.41 | 9.29 | 9.16 | 7.4 |  | 9.5 | No
2021-05-09 | 7:40 | 125 | 10.26 |  |  | 2212439 | 125.2477 |  |  |  |  | 1760689875 | 1064.1837 |  | 977 | 3909576250 | 897.1429 | 893 | 5413.74 | 5418.1 | 9.14 | 8.97 | 9.55 | 9.52 | 9.49 | 9.39 | 9.27 | 7.45 |  | 9.5 | No
2021-05-10 | 7:26 | 125 | 10.26 |  |  | 2213146 | 125.0581 |  |  |  |  | 1762183500 | 1047.4229 |  | 859 | 3910825000 | 875.7013 | 859 | 5413.7 | 5418.06 | 9.26 | 9.07 | 9.57 | 9.6 | 9.53 | 9.45 | 9.33 | 7.49 |  | 9.5 | No
2021-05-11 | 7:45 | 125 | 10.27 |  |  | 2213874 | 125.2813 |  |  |  |  | 1763718750 | 1052.2618 |  | 994 | 3912086250 | 864.462 | 871 | 5413.71 | 5418.07 | 9.24 | 9.04 | 9.56 | 9.58 | 9.48 | 9.45 | 9.33 | 7.42 |  | 9.5 | No
2021-05-12 | 12:10 | 125 | 10.09 |  |  | 2214691 | 125.4589 |  |  |  |  | 1765439250 | 1009.0909 |  | 1096 | 3913510250 | 835.1906 | 828 | 5413.83 | 5418.19 | 9.27 | 9.06 | 9.51 | 9.55 | 9.43 | 9.4 | 9.28 | 7.49 |  | 9.5 | No
2021-05-13 | 11:10 | 125 | 10.2 |  |  | 2215354 | 125.1179 |  |  |  |  | 1766839250 | 1014.4928 |  | 1083 | 3914673500 | 842.9348 | 848 | 5413.86 | 5418.22 | 9.29 | 9.06 | 9.5 | 9.51 | 9.31 | 9.3 | 9.15 | 7.47 |  | 9.5 | No
2021-05-14 | 8:20 | 125 | 10.14 |  |  | 2215922 | 125.4209 |  |  |  |  | 1768035750 | 942.126 |  | 996 | 3915692000 | 801.9685 | 786 | 5414.11 | 5418.47 | 9.28 | 9.1 | 9.52 | 9.52 | 9.39 | 9.36 | 9.29 | 7.45 |  | 9.5 | No
2021-05-15 | 8:33 | 125 | 10.15 |  |  | 2216616 | 125.3605 |  |  |  |  | 1769498375 | 1006.6242 |  | 1022 | 3916884750 | 820.8878 | 839 | 5414.1 | 5418.46 | 9.32 | 9.16 | 9.53 | 9.54 | 9.41 | 9.38 | 9.29 | 7.49 |  | 9.5 | No
2021-05-16 | 8:55 | 125 | 10.21 |  |  | 2217305 | 125.5193 |  |  |  |  | 1770948625 | 991.9631 |  | 967 | 3918105000 | 834.6443 | 830 | 5414.11 | 5418.47 | 9.31 | 9.17 | 9.54 | 9.55 | 9.45 | 9.39 | 9.3 | 7.43 |  | 9.5 | No
2021-05-17 | 9:30 | 125 | 10.16 |  |  | 2217996 | 125.2467 |  |  |  |  | 1772406250 | 988.2203 |  | 959 | 3919313000 | 818.9831 | 820 | 5414.11 | 5418.47 | 9.3 | 9.15 | 9.48 | 9.48 | 9.37 | 9.31 | 9.27 | 7.44 | Lime rate increased to 130mg/l @ 13:00 due to D4 dredging activities, Lime rate increased to 135mg/l @13:50, Increased to 140mg/l @14:50 Decreased to 130mg/l @1800 | 9.5 | No
2021-05-18 | 8:40 | 130 | 10.04 |  |  | 2218616 | 131.0698 |  |  |  |  | 1773656000 | 899.1007 |  | 779 | 3920389500 | 774.4604 | 733 | 5413.87 | 5418.23 | 9.32 | 9.15 | 9.5 | 9.49 | 9.33 | 9.3 | 9.29 | 7.43 |  | 9.5 | No
2021-05-19 | 8:00 | 130 | 10.2 |  |  | 2219212 | 130.3912 |  |  |  |  | 1774863625 | 862.5893 |  | 785 | 3921347000 | 683.9286 | 691 | 5413.91 | 5418.27 | 9.28 | 9.15 | 9.54 | 9.51 | 9.32 | 9.29 | 9.31 | 7.43 |  | 9.5 | No
2021-05-20 | 8:35 | 130 | 10.26 |  |  | 2219857 | 129.4659 |  |  |  |  | 1776179875 | 892.3729 |  | 1487 | 3922349750 | 679.8305 | 744 | 5414.11 | 5418.47 | 9.25 | 9.13 | 9.59 | 9.54 | 9.33 | 9.27 | 9.24 | 7.5 | IPS pump was shut OFF @11:40 for 1 hour. | 9.5 | No
2021-05-21 | 10:05 | 130 | 10.35 |  |  | 2220645 | 130.578 |  |  |  |  | 1777774250 | 1042.0752 |  | 1800 | 3923641750 | 844.4444 | 874 | 5413.83 | 5418.19 | 9.32 | 9.19 | 9.7 | 9.63 | 9.41 | 9.33 | 9.33 | 7.42 |  | 9.5 | No
2021-05-22 | 9:20 | 130 | 10.4 |  |  | 2221441 | 129.9475 |  |  |  |  | 1779392625 | 1160.1254 |  | 1261 | 3925052750 | 1011.4695 | 1047 | 5413.91 | 5418.27 | 9.28 | 9.18 | 9.76 | 9.7 | 9.58 | 9.46 | 9.38 | 7.49 | lime rate decreased to 125mg/l @ 9:30 | 9.5 | No
2021-05-23 | 8:30 | 125 | 10.32 |  |  | 2222200 | 125.6739 |  |  |  |  | 1780988250 | 1147.9317 |  | 1258 | 3926476750 | 1024.4604 | 1011 | 5413.93 | 5418.29 | 9.37 | 9.28 | 9.75 | 9.73 | 9.58 | 9.5 | 9.41 | 7.55 |  | 9.5 | No
2021-05-24 | 9:40 | 130 | 10.37 |  |  | 2223044 | 125.6256 |  |  |  |  | 1782763250 | 1175.4967 |  | 777 | 3928083250 | 1063.9073 | 1067 | 5413.83 | 5418.19 | 9.45 | 9.23 | 9.75 | 9.75 | 9.65 | 9.52 | 9.27 | 7.41 | Lime rate increased to 130mg/l @ 7:30 | 9.5 | No
2021-05-25 | 8:20 | 130 | 10.31 |  |  | 2223733 | 130.4438 |  |  |  |  | 1784158750 | 1026.1029 |  | 784 | 3929312750 | 904.0441 | 918 | 5414 | 5418.36 | 9.52 | 9.32 | 9.69 | 9.69 | 9.53 | 9.51 | 9.45 | 7.48 |  | 9.5 | No
2021-05-26 | 8:00 | 130 | 10.4 |  |  | 2224472 | 130.0979 |  |  |  |  | 1785659500 | 1056.8662 |  | 793 | 3930602500 | 908.2746 | 972 | 5414.11 | 5418.47 | 9.46 | 9.31 | 9.66 | 9.67 | 9.51 | 9.5 | 9.4 | 7.4 |  | 9.5 | No
2021-05-27 | 8:15 | 130 | 10.42 |  |  | 2225187 | 130.4808 |  |  |  |  | 1787107250 | 995.0172 |  | 790 | 3931894250 | 887.8007 | 906 | 5413.97 | 5418.33 | 9.42 | 9.33 | 9.5 | 9.67 | 9.48 | 9.46 | 9.4 | 7.33 | lime rate decreased to 125mg/l @ 7:00 am | 9.5 | No
2021-05-28 | 9:00 | 125 | 10.23 |  |  | 2225845 | 129.8071 |  |  |  |  | 1788446500 | 901.8519 |  | 1059 | 3933115500 | 822.3906 | 771 | 5414.14 | 5418.5 | 9.5 | 9.32 | 9.71 | 9.7 | 9.47 | 9.46 | 9.41 | 7.44 |  | 9.5 | No
2021-05-29 | 7:10 | 125 | 10.03 |  |  | 2226537 | 125.8922 |  |  |  |  | 1789898750 | 1091.9173 |  | 1086 | 3934213750 | 825.7519 | 903 | 5414.15 | 5418.51 | 9.38 | 9.22 | 9.61 | 9.58 | 9.36 | 9.33 | 9.28 | 7.41 |  | 9.5 | No
2021-05-30 | 6:55 | 125 | 10.04 |  |  | 2227319 | 125.2152 |  |  |  |  | 1791548750 | 1157.8947 |  | 949 | 3935542750 | 932.6316 | 961 | 5414.09 | 5418.45 | 9.4 | 9.24 | 9.63 | 9.61 | 9.38 | 9.34 | 9.3 | 7.36 |  | 9.5 | No
2021-05-31 | 7:00 | 125 | 10.02 |  |  | 2228108 | 125.2731 |  |  |  |  | 1793212750 | 1151.5571 |  | 945 | 3936919750 | 952.9412 | 960 | 5414.05 | 5418.41 | 9.42 | 9.27 | 9.58 | 9.58 | 9.36 | 9.34 | 9.28 | 7.41 |  | 9.5 | No
2021-06-01 | 8:30 | 125 | 10.05 |  |  | 2228925 | 125.1044 |  |  |  |  | 1794938125 | 1127.6961 |  | 786 | 3938377750 | 952.9412 | 948 | 5413.91 | 5418.27 | 9.35 | 9.23 | 9.54 | 9.54 | 9.38 | 9.31 | 9.15 | 7.6 |  | 9.5 | No
2021-06-02 | 8:05 | 125 | 10.1 |  |  | 2229521 | 125.2321 |  |  |  |  | 1796195500 | 888.6042 |  | 792 | 3939548500 | 827.3852 | 761 | 5414.05 | 5418.41 | 9.25 | 9.13 | 9.45 | 9.45 | 9.26 | 9.22 | 9.27 | 7.37 | lime rate increased to 130mg/l @ 12:00 | 9.5 | No
2021-06-03 | 9:20 | 130 | 10.08 |  |  | 2230215 | 129.7287 |  |  |  |  | 1797608875 | 932.9208 |  | 1046 | 3940657750 | 732.1782 | 790 | 5414.12 | 5418.48 | 9.23 | 9.15 | 9.4 | 9.39 | 9.21 | 9.19 | 9.21 | 7.34 | lime rate decreased to 125mg/l @ 9:30 | 9.5 | No
2021-06-04 | 7:40 | 125 | 10.11 |  |  | 2230952 | 125.0685 |  |  |  |  | 1799165750 | 1161.847 |  | 1089 | 3941861250 | 898.1343 | 923 | 5413.88 | 5418.24 | 9.18 | 9.13 | 9.36 | 9.33 | 9.2 | 9.15 | 9.18 | 7.31 | Lime rate increased to 130mg/l @ 9:00 | 9.5 | No
2021-06-05 | 10:15 | 130 | 10.09 |  |  | 2231804 | 130.1809 |  |  |  |  | 1800894875 | 1084.0909 |  | 1130 | 3943274750 | 886.2069 | 879 | 5413.85 | 5418.21 | 9.21 | 9.12 | 9.37 | 9.35 | 9.32 | 9.24 | 9.23 | 7.37 |  | 9.5 | No
2021-06-06 | 9:15 | 130 | 10.18 |  |  | 2232513 | 130.2631 |  |  |  |  | 1802332875 | 1042.029 |  | 1128 | 3944418250 | 828.6232 | 810 | 5413.88 | 5418.24 | 9.17 | 9.11 | 9.41 | 9.36 | 9.29 | 9.21 | 9.22 | 7.43 |  | 9.5 | No
2021-06-07 | 8:55 | 130 | 10.14 |  |  | 2233259 | 129.4328 |  |  |  |  | 1803855625 | 1072.3592 |  | 1080 | 3945596750 | 829.9296 | 836 | 5413.84 | 5418.2 | 9.19 | 9.13 | 9.51 | 9.47 | 9.38 | 9.3 | 9.26 | 7.57 |  | 9.5 | No
2021-06-08 | 7:45 | 130 | 10.15 |  |  | 2233988 | 131.3012 |  |  |  |  | 1805322500 | 1070.7117 |  | 1162 | 3946743250 | 836.8613 | 869 | 5413.84 | 5418.2 | 9.28 | 9.2 | 9.59 | 9.52 | 9.44 | 9.3 | 9.29 | 7.45 |  | 9.5 | No
2021-06-09 | 9:45 | 130 | 10.2 |  |  | 2234904 | 130.4361 |  |  |  |  | 1807177875 | 1189.3429 |  | 944 | 3948192250 | 928.8462 | 976 | 5413.82 | 5418.18 | 9.17 | 9.1 | 9.45 | 9.43 | 9.37 | 9.28 | 9.24 | 7.4 |  | 9.5 | No
2021-06-10 | 7:10 | 130 | 10.1 |  |  | 2235619 | 130.312 |  |  |  |  | 1808627500 | 1128.1128 |  | 1259 | 3949389250 | 931.5175 | 902 | 5413.78 | 5418.14 | 9.2 | 9.12 | 9.45 | 9.42 | 9.32 | 9.31 | 9.25 | 7.38 |  | 9.5 | No
2021-06-11 | 8:15 | 130 | 10.42 |  |  | 2236440 | 130.3833 |  |  |  |  | 1810291125 | 1105.3987 |  | 1103 | 3950788250 | 929.5681 | 971 | 5413.88 | 5418.24 | 9.26 | 9.12 | 9.52 | 9.44 | 9.41 | 9.34 | 9.18 | 7.28 |  | 9.5 | No
2021-06-12 | 7:00 | 130 | 10.19 |  |  | 2237159 | 130.3777 |  |  |  |  | 1811748125 | 1067.3993 |  | 1040 | 3952041750 | 918.315 | 873 | 5413.88 | 5418.24 | 9.25 | 9.1 | 9.49 | 9.45 | 9.4 | 9.37 | 9.31 | 7.29 |  | 9.5 | No
2021-06-13 | 12:00 | 130 | 10.28 |  |  | 2238083 | 130.4329 |  |  |  |  | 1813619750 | 1075.6466 |  | 1118 | 3953517250 | 847.9885 | 843 | 5413.83 | 5418.19 | 9.22 | 9.1 | 9.46 | 9.51 | 9.4 | 9.36 | 9.28 | 7.4 |  | 9.5 | No
2021-06-14 | 8:40 | 130 | 10.22 |  |  | 2238739 | 130.3248 |  |  |  |  | 1814949625 | 1072.4798 |  | 1029 | 3954513000 | 803.0242 | 823 | 5413.86 | 5418.22 | 9.26 | 9.12 | 9.52 | 9.46 | 9.41 | 9.35 | 9.28 | 7.35 |  | 9.5 | No
2021-06-15 | 9:15 | 130 | 10.28 |  |  | 2239569 | 129.1156 |  |  |  |  | 1816648000 | 1151.4407 |  | 1189 | 3955727000 | 823.0508 | 812 | 5413.88 | 5418.24 | 9.15 | 9.12 | 9.55 | 9.51 | 9.43 | 9.35 | 9.28 | 7.38 |  | 9.5 | No
2021-06-16 | 8:30 | 130 | 10.16 |  |  | 2240358 | 130.0808 |  |  |  |  | 1818250500 | 1148.7455 |  | 1051 | 3956855250 | 808.7814 | 827 | 5413.85 | 5418.21 | 9.22 | 9.11 | 9.62 | 9.53 | 9.49 | 9.38 | 9.3 | 7.43 |  | 9.5 | No
2021-06-17 | 6:45 | 130 | 10.22 |  |  | 2241056 | 130.9629 |  |  |  |  | 1819658625 | 1054.7753 |  | 1082 | 3957902500 | 784.4569 | 739 | 5413.86 | 5418.22 | 9.35 | 9.21 | 9.64 | 9.58 | 9.56 | 9.41 | 9.32 | 7.45 |  | 9.5 | No
2021-06-18 | 7:30 | 130 | 10.22 |  |  | 2241855 | 129.507 |  |  |  |  | 1821288625 | 1097.6431 |  | 1071 | 3959023500 | 754.8822 | 799 | 5413.9 | 5418.26 | 9.29 | 9.14 | 9.64 | 9.61 | 9.49 | 9.45 | 9.36 | 7.4 |  | 9.5 | No
2021-06-19 | 8:40 | 130 | 10.36 |  |  | 2242683 | 131.042 |  |  |  |  | 1822958000 | 1105.5464 |  | 1110 | 3960296000 | 842.7152 | 880 | 5413.9 | 5418.26 | 9.26 | 9.16 | 9.62 | 9.59 | 9.49 | 9.44 | 9.33 | 7.37 |  | 9.5 | No
2021-06-20 | 7:25 | 130 | 10.42 |  |  | 2243403 | 125.9557 |  |  |  |  | 1824468250 | 1106.4103 |  | 938 | 3961475000 | 863.7363 | 866 | 5413.82 | 5418.18 | 9.32 | 9.2 | 9.59 | 9.57 | 9.44 | 9.45 | 9.35 | 7.38 | Lime rate decreased to 125mg/l @ 8:00 | 9.5 | No
2021-06-21 | 12:20 | 125 | 10.23 |  |  | 2244312 | 125.6223 |  |  |  |  | 1826380000 | 1101.8732 |  | 1156 | 3963014500 | 887.3199 | 890 | 5413.872 | 5418.232 | 9.36 | 9.19 | 9.58 | 9.61 | 9.5 | 9.47 | 9.37 | 7.27 |  | 9.5 | No
2021-06-22 | 8:45 | 125 | 9.96 |  |  | 2244965 | 125.3346 |  |  |  |  | 1827756500 | 1123.6735 |  | 1017 | 3964088750 | 876.9388 | 902 | 5413.94 | 5418.3 | 9.36 | 9.22 | 9.52 | 9.54 | 9.45 | 9.43 | 9.35 | 7.24 |  | 9.5 | No
2021-06-23 | 11:50 | 125 | 9.93 |  |  | 2245825 | 125.1343 |  |  |  |  | 1829572250 | 1117.3846 |  | 1005 | 3965526250 | 884.6154 | 877 | 5413.86 | 5418.22 | 9.33 | 9.25 | 9.51 | 9.52 | 9.47 | 9.43 | 9.36 | 7.48 |  | 9.5 | No
2021-06-24 | 14:00 | 125 | 10.08 |  |  | 2246600 | 125.7326 |  |  |  |  | 1831200750 | 1037.2611 |  | 966 | 3966832750 | 832.1656 | 819 | 5413.85 | 5418.21 | 9.35 | 9.27 | 9.53 | 9.55 | 9.5 | 9.45 | 9.36 | 7.58 |  | 9.5 | No
2021-06-25 | 9:00 | 125 | 10.07 |  |  | 2247159 | 125.4919 |  |  |  |  | 1832377625 | 1032.3465 |  | 1086 | 3967748000 | 802.8509 | 796 | 5413.87 | 5418.23 | 9.2 | 9.14 | 9.38 | 9.38 | 9.34 | 9.33 | 9.28 | 7.51 |  | 9.5 | No
2021-06-26 | 6:20 | 125 | 10.06 |  |  | 2247780 | 125.6389 |  |  |  |  | 1833683500 | 1020.2148 |  | 1055 | 3968753700 | 785.7031 | 793 | 5413.86 | 5418.22 | 9.28 | 9.19 | 9.45 | 9.43 | 9.37 | 9.37 | 9.3 | 7.39 |  | 9.5 | No
2021-06-27 | 6:15 | 125 | 10.01 |  |  | 2248477 | 125.5804 |  |  |  |  | 1835149875 | 1021.8641 |  | 984 | 3969893000 | 793.9373 | 792 | 5413.86 | 5418.22 | 9.28 | 9.18 | 9.47 | 9.43 | 9.37 | 9.38 | 9.31 | 7.37 |  | 9.5 | No
2021-06-28 | 8:40 | 125 | 10.07 |  |  | 2249241 | 125.0132 |  |  |  |  | 1836764500 | 1018.6909 |  | 1052 | 3971153000 | 794.9527 | 791 | 5413.86 | 5418.22 | 9.23 | 9.15 | 9.44 | 9.41 | 9.36 | 9.37 | 9.31 | 7.38 |  | 9.5 | No
2021-06-29 | 9:05 | 125 | 10.02 |  |  | 2249972 | 125.3892 |  |  |  |  | 1838304750 | 1051.3652 |  | 1092 | 3972318750 | 795.7338 | 813 | 5413.85 | 5418.21 | 9.24 | 9.14 | 9.41 | 9.4 | 9.34 | 9.36 | 9.29 | 7.34 |  | 9.5 | No
2021-06-30 | 11:25 | 125 | 9.97 |  |  | 2250763 | 125.4964 |  |  |  |  | 1839970000 | 1053.9557 |  | 1073 | 3973616250 | 821.2025 | 821 | 5413.87 | 5418.23 | 9.2 | 9.13 | 9.43 | 9.4 | 9.4 | 9.35 | 9.24 | 7.34 |  | 9.5 | No

## MSD
Do Not Move, Add, or Remove any Columns After "Date" without Updating the Column Name Definitions - Do Not Remove the "Count" that the Definitions Reference --> | [12 empty] | Do Not Delete! |  | Do Not Delete!
Date | Time | Flow Rate (gpm) South/North | Flow Rate Post | Total Flow (gallons) South/North | Average (gpm) | West Vault Level (ft) | East Vault Level (ft) | New Vault Level (inches) | Comments | MSD-V1W Elev (ft) | MSD-V1E Elev (ft) | MSD-V2W Elev (ft) | Count Chart Cells | 182
[10 empty] | 5444.99 | 5444.99 | 5439.4
2020-12-31 | 7:20 | 426 |  | 1724597017 | 426.5152 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-01-01 | 7:40 | 431 |  | 1725219391 | 426.2836 |  |  | 43.66 | Operating dry vault pumps, north and south lines.
2021-01-02 | 7:10 | 425 |  | 1725824329 | 429.034 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-03 | 9:00 | 433 |  | 1726489204 | 428.9516 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-04 | 10:30 | 427 |  | 1727139079 | 424.7549 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-01-05 | 10:30 | 418 |  | 1727752017 | 425.6514 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-06 | 9:10 | 422 |  | 1728328454 | 423.8507 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-01-07 | 10:45 | 428 |  | 1728979517 | 424.1453 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-08 | 9:00 | 422 |  | 1729544141 | 422.9393 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-01-09 | 7:45 | 426 |  | 1730122391 | 423.6264 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-10 | 7:45 | 408 |  | 1730731329 | 422.8736 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-01-11 | 9:00 | 416 |  | 1731369391 | 421.163 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-01-12 | 10:20 | 425 |  | 1732009954 | 421.423 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-13 | 9:30 | 419 |  | 1732594517 | 420.5489 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-14 | 9:40 | 425 |  | 1733201829 | 418.8359 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-01-15 | 9:00 | 414 |  | 1733785704 | 417.0536 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-01-16 | 7:45 | 416 |  | 1734360579 | 421.1538 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-01-17 | 7:35 | 416 |  | 1734957016 | 417.0888 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-01-18 | 8:35 | 410 |  | 1735588392 | 420.9173 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-01-19 | 7:45 | 416 |  | 1736168266 | 417.1755 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-01-20 | 9:05 | 414 |  | 1736802829 | 417.4757 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-01-21 | 10:30 | 417 |  | 1737440516 | 418.1554 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-01-22 | 9:30 | 420 |  | 1738014517 | 415.9428 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-01-23 | 9:30 | 414 |  | 1738616829 | 418.2722 |  |  | 43.56 | Operating dry vault pumps, north and south lines.
2021-01-24 | 14:00 | 420 |  | 1739328392 | 416.1187 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-01-25 | 11:30 | 414 |  | 1739867454 | 417.8775 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-01-26 | 10:15 | 416 |  | 1740434517 | 415.4308 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-01-27 | 9:30 | 411 |  | 1741013642 | 415.1434 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-01-28 | 8:30 | 414 |  | 1741583891 | 413.2239 |  |  | 43.56 | Operating dry vault pumps, north and south lines. , BRW flow switched to Drying bed discharge for MSD jetting
2021-01-29 | 9:00 | 664 |  | 1742476563 | 607.2599 |  |  | 43.96 | Operating dry vault pumps, north and south lines. , BRW flow switched to Drying bed discharge for MSD jetting, Returned to HCC discharge
2021-01-30 | 8:40 | 468 |  | 1743158251 | 480.062 |  |  | 43.62 | Operating dry vault pumps, north and south lines.
2021-01-31 | 9:20 | 468 |  | 1743861439 | 475.127 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-02-01 | 10:00 | 465 |  | 1744553563 | 467.6514 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-02-02 | 10:00 | 466 |  | 1745221501 | 463.8458 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-02-03 | 9:25 | 477 |  | 1745886126 | 473.0427 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-02-04 | 9:05 | 474 |  | 1746566564 | 479.1817 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-02-05 | 9:40 | 472 |  | 1747255689 | 467.2034 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-02-06 | 7:40 | 472 |  | 1747858063 | 456.3439 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-02-07 | 8:00 | 466 |  | 1748545813 | 471.0616 |  |  | 43.53 | Operating dry vault pumps, north and south lines.
2021-02-08 | 10:25 | 460 |  | 1749274564 | 459.7798 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-02-09 | 10:30 | 462 |  | 1749944563 | 463.6671 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-02-10 | 9:30 | 459 |  | 1750573313 | 455.6159 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-02-11 | 11:00 | 467 |  | 1751273314 | 457.517 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-02-12 | 9:00 | 449 |  | 1751874751 | 455.6341 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-02-13 | 8:55 | 455 |  | 1752532001 | 458.0139 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-02-14 | 9:40 | 450 |  | 1753209438 | 456.1865 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-02-15 | 11:50 | 449 |  | 1753926501 | 456.728 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-02-16 | 12:35 | 461 |  | 1754600688 | 453.998 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-02-17 | 8:40 | 462 |  | 1755148876 | 454.9278 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-02-18 | 8:30 | 443 |  | 1755796188 | 452.6657 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-02-19 | 9:00 | 453 |  | 1756462438 | 453.2313 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-02-20 | 12:35 | 452 |  | 1757218501 | 456.8356 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-02-21 | 8:45 | 452 |  | 1757769251 | 455.1653 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-02-22 | 9:50 | 449 |  | 1758452251 | 453.8206 |  |  | 43.66 | Operating dry vault pumps, north and south lines.
2021-02-23 | 10:00 | 470 |  | 1759120063 | 460.56 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-02-24 | 9:05 | 463 |  | 1759769251 | 468.7278 |  |  | 47.4 | Operating dry vault pumps, north and south lines.
2021-02-25 | 8:45 | 466 |  | 1760432938 | 467.3852 |  |  | 44.97 | Operating dry vault pumps, north and south lines.
2021-02-26 | 7:50 | 455 |  | 1761072813 | 462.0036 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-02-27 | 7:45 | 462 |  | 1761727001 | 455.8801 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-02-28 | 7:30 | 447 |  | 1762373376 | 453.5965 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-03-01 | 8:05 | 450 |  | 1763043689 | 454.4495 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-02 | 9:10 | 446 |  | 1763709376 | 442.3169 |  |  | 43.06 | Operating dry vault pumps, north and south lines.
2021-03-03 | 8:30 | 471 |  | 1764357564 | 462.9914 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-03-04 | 8:25 | 484 |  | 1765054689 | 485.8014 |  |  | 43.66 | Operating dry vault pumps, north and south lines.
2021-03-05 | 9:50 | 493 |  | 1765765814 | 466.3115 |  |  | 44.62 | Operating dry vault pumps, north and south lines.
2021-03-06 | 8:25 | 476 |  | 1766451876 | 506.3188 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-03-07 | 8:40 | 480 |  | 1767156751 | 484.4502 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-08 | 9:25 | 483 |  | 1767872189 | 481.7764 |  |  | 43.6 | Operating dry vault pumps, north and south lines. Started taking water from NST pump test @8:00 North/South pumps OFF using portable diesel pump from 8am to 4pm
2021-03-09 | 10:20 | 604 |  | 1768604938 | 490.1331 |  |  | 52.57 | Operating dry vault pumps, north and south lines. North/South pumps OFF using portable diesel pump from 8am to 4pm
2021-03-10 | 7:30 | 492 |  | 1769240376 | 500.3449 |  |  | 48.09 | Operating dry vault pumps, north and south lines North/South pumps OFF using portable diesel pump from 8am to 4pm
2021-03-11 | 9:05 | 590 |  | 1770047063 | 525.529 |  |  | 48.78 | Operating dry vault pumps, north and south lines. North/South pumps OFF using portable diesel pump from 8am to 4pm
2021-03-12 | 8:30 | 467 |  | 1770729189 | 485.4989 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-03-13 | 9:30 | 468 |  | 1771427501 | 465.5413 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-03-14 | 6:15 | 471 |  | 1771988689 | 450.7534 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-15 | 9:20 | 469 |  | 1772758876 | 473.9612 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-16 | 10:30 | 481 |  | 1773477689 | 476.0351 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-03-17 | 9:25 | 470 |  | 1774128564 | 473.3636 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-03-18 | 9:00 | 465 |  | 1774797876 | 473.012 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-03-19 | 9:00 | 484 |  | 1775477939 | 472.266 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-03-20 | 8:20 | 478 |  | 1776152314 | 481.6964 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-03-21 | 9:40 | 462 |  | 1776861813 | 466.7757 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-03-22 | 9:00 | 457 |  | 1777507188 | 460.9821 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-23 | 10:20 | 449 |  | 1778195064 | 452.55 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-24 | 7:40 | 448 |  | 1778769376 | 448.6812 |  |  | 43.66 | Operating dry vault pumps, north and south lines.
2021-03-25 | 9:05 | 445 |  | 1779452813 | 448.1554 |  |  | 43.62 | Operating dry vault pumps, north and south lines.
2021-03-26 | 7:10 | 446 |  | 1780039501 | 442.7834 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-03-27 | 8:00 | 444 |  | 1780707814 | 448.5322 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-28 | 8:10 | 445 |  | 1781346751 | 440.6462 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-03-29 | 9:45 | 443 |  | 1782027439 | 443.445 |  |  | 43.66 | Operating dry vault pumps, north and south lines.
2021-03-30 | 10:45 | 442 |  | 1782695939 | 445.6667 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-03-31 | 8:00 | 444 |  | 1783258438 | 441.1757 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-01 | 10:40 | 444 |  | 1783965564 | 441.9537 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-02 | 8:45 | 441 |  | 1784552188 | 442.7351 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-04-03 | 9:00 | 439 |  | 1785196251 | 442.655 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-04-04 | 8:55 | 441 |  | 1785829876 | 441.5505 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-05 | 10:20 | 444 |  | 1786508439 | 444.9593 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-06 | 10:10 | 451 |  | 1787164001 | 458.435 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-07 | 8:45 | 446 |  | 1787776314 | 451.8915 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-08 | 6:55 | 447 |  | 1788372751 | 448.4489 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-09 | 9:15 | 447 |  | 1789076501 | 445.4114 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-10 | 7:20 | 444 |  | 1789662376 | 442.1698 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-11 | 7:15 | 443 |  | 1790294939 | 440.8105 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-04-12 | 11:20 | 438 |  | 1791038126 | 441.0605 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-04-13 | 8:45 | 434 |  | 1791605564 | 441.586 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-04-14 | 9:15 | 438 |  | 1792247751 | 436.8619 |  |  | 43.62 | Operating dry vault pumps, north and south lines.
2021-04-15 | 8:20 | 452 |  | 1792856563 | 439.5755 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-04-16 | 9:15 | 438 |  | 1793511251 | 437.9184 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-04-17 | 10:00 | 443 |  | 1794165689 | 440.699 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-04-18 | 9:05 | 445 |  | 1794773189 | 438.6282 |  |  | 43.62 | Operating dry vault pumps, north and south lines.
2021-04-19 | 9:15 | 435 |  | 1795404001 | 435.0428 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-04-20 | 8:45 | 451 |  | 1796031501 | 445.0355 |  |  | 43.66 | Operating dry vault pumps, north and south lines.
2021-04-21 | 9:15 | 453 |  | 1796673751 | 436.9048 |  |  | 43.67 | Operating dry vault pumps, north and south lines.
2021-04-22 | 8:30 | 443 |  | 1797283126 | 436.828 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-04-23 | 8:25 | 441 |  | 1797917813 | 442.2906 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-04-24 | 8:10 | 444 |  | 1798547939 | 442.1937 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-04-25 | 7:30 | 446 |  | 1799166439 | 441.7857 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-04-26 | 10:10 | 454 |  | 1799881564 | 446.9531 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-04-27 | 8:55 | 447 |  | 1800496501 | 450.5033 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-04-28 | 8:55 | 440 |  | 1801136376 | 444.3576 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-04-29 | 9:05 | 439 |  | 1801778751 | 443.0172 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-04-30 | 10:15 | 439 |  | 1802446564 | 442.2603 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-05-01 | 7:10 | 446 |  | 1803001626 | 442.2805 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-05-02 | 7:00 | 445 |  | 1803631188 | 440.2531 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-05-03 | 8:20 | 444 |  | 1804301563 | 441.0362 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-05-04 | 9:55 | 439 |  | 1804978876 | 441.2463 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-05-05 | 9:00 | 439 |  | 1805586313 | 438.5827 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-05-06 | 9:15 | 438 |  | 1806220938 | 436.1684 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-05-07 | 12:15 | 435 |  | 1806928938 | 437.037 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-05-08 | 11:15 | 448 |  | 1807539501 | 442.437 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-05-09 | 7:40 | 445 |  | 1808086813 | 446.7853 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-05-10 | 7:26 | 437 |  | 1808718313 | 442.8471 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-05-11 | 8:30 | 438 |  | 1809357751 | 425.1582 |  |  | 43.61 | Operating dry vault pumps, north and south lines.
2021-05-12 | 12:10 | 441 |  | 1810103001 | 448.9458 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-05-13 | 11:10 | 434 |  | 1810701938 | 434.0123 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-05-14 | 8:20 | 432 |  | 1811251626 | 432.8252 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-05-15 | 8:30 | 432 |  | 1811880063 | 433.4048 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-05-16 | 8:55 | 434 |  | 1812510563 | 430.3754 |  |  | 43.62 | Operating dry vault pumps, north and south lines.
2021-05-17 | 9:20 | 431 |  | 1813145126 | 433.1488 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-05-18 | 8:40 | 428 |  | 1813750313 | 432.2764 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-05-19 | 8:00 | 427 |  | 1814348313 | 427.1429 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-05-20 | 8:35 | 427 |  | 1814983313 | 430.5085 |  |  | 43.57 | Operating dry vault pumps, north and south lines.
2021-05-21 | 10:05 | 460 |  | 1815678751 | 454.5346 |  |  | 45.33 | Operating dry vault pumps, north and south lines.
2021-05-22 | 9:20 | 459 |  | 1816311188 | 453.3599 |  |  | 46.21 | Operating dry vault pumps, north and south lines.
2021-05-23 | 8:30 | 459 |  | 1816947813 | 458.0036 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-05-24 | 9:40 | 458 |  | 1817636813 | 456.2914 |  |  | 50.8 | Operating dry vault pumps, north and south lines.
2021-05-25 | 8:20 | 450 |  | 1818258501 | 457.1235 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-05-26 | 8:00 | 450 |  | 1818898376 | 450.6162 |  |  | 44.92 | Operating dry vault pumps, north and south lines.
2021-05-27 | 8:15 | 454 |  | 1819565251 | 458.3333 |  |  | 48.57 | Operating dry vault pumps, north and south lines.
2021-05-28 | 9:00 | 458 |  | 1820244938 | 457.7017 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-05-29 | 7:10 | 454 |  | 1820840813 | 448.0263 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-05-30 | 6:55 | 438 |  | 1821473126 | 443.7284 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-05-31 | 7:00 | 435 |  | 1822106626 | 438.4083 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-01 | 8:30 | 436 |  | 1822777501 | 438.4804 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-06-02 | 8:05 | 432 |  | 1823390688 | 433.3477 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-06-03 | 9:20 | 433 |  | 1824044813 | 431.7657 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-06-04 | 7:40 | 436 |  | 1824622688 | 431.25 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-06-05 | 10:15 | 426 |  | 1825305626 | 428.1743 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-06-06 | 9:15 | 433 |  | 1825898063 | 429.3022 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-07 | 8:55 | 427 |  | 1826512001 | 432.3507 |  |  | 43.58 | Operating dry vault pumps, north and south lines.
2021-06-08 | 7:45 | 424 |  | 1827092126 | 423.4489 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-06-09 | 9:45 | 424 |  | 1827760001 | 428.125 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-10 | 7:10 | 428 |  | 1828308813 | 427.0911 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-11 | 8:15 | 452 |  | 1828967501 | 437.6664 |  |  | 46.24 | Operating dry vault pumps, north and south lines.
2021-06-12 | 7:00 | 443 |  | 1829581313 | 449.6791 |  |  | 43.57 | Operating dry vault pumps, north and south lines.
2021-06-13 | 12:00 | 438 |  | 1830343188 | 437.8592 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-06-14 | 8:40 | 427 |  | 1830861571 | 418.0508 |  |  | 43.6 | Operating dry vault pumps, north and south lines.
2021-06-15 | 9:15 | 430 |  | 1831505626 | 436.6475 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-06-16 | 8:30 | 445 |  | 1832122938 | 442.5176 |  |  | 43.64 | Operating dry vault pumps, north and south lines. Switched to Drying bed discharge for jetting activities @ 9:00 switched back @ 15:40
2021-06-17 | 6:45 | 448 |  | 1832636438 | 384.6442 |  |  | 56.61 | Operating dry vault pumps, north and south lines.
2021-06-18 | 7:30 | 468 |  | 1833273813 | 429.2088 |  |  | 43.96 | Operating dry vault pumps, north and south lines.
2021-06-19 | 8:40 | 464 |  | 1833975376 | 464.6113 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-20 | 7:25 | 459 |  | 1834609251 | 464.3773 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-06-21 | 12:20 | 460 |  | 1835415188 | 464.517 |  |  | 43.59 | Operating dry vault pumps, north and south lines.
2021-06-22 | 8:45 | 460 |  | 1835981876 | 462.6024 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-23 | 11:50 | 459 |  | 1836732813 | 462.1151 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-24 | 14:00 | 454 |  | 1837448876 | 456.0911 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-06-25 | 9:00 | 450 |  | 1837974438 | 461.0193 |  |  | 43.65 | Operating dry vault pumps, north and south lines.
2021-06-26 | 6:20 | 452 |  | 1838547688 | 447.8516 |  |  | 43.64 | Operating dry vault pumps, north and south lines.
2021-06-27 | 6:15 | 449 |  | 1839192188 | 449.1289 |  |  | 43.63 | Operating dry vault pumps, north and south lines.
2021-06-28 | 8:40 | 442 |  | 1839905938 | 450.3155 |  |  | 43.62 | Operating dry vault pumps, north and south lines.
2021-06-29 | 9:05 | 441 |  | 1840558938 | 445.7338 |  |  | 43.62 | Operating dry vault pumps, north and south lines.
2021-06-30 | 11:25 | 443 |  | 1841261821 | 444.8627 |  |  | 43.56 | Operating dry vault pumps, north and south lines.

## BRW
Do Not Move, Add, or Remove any Columns After "Date" without Updating the Column Name Definitions - Do Not Remove the "Count" that the Definitions Reference --> | [22 empty] | COUNT
Date | Time | 00 Pond Flow Rate (gpm) | 00 Pond Total Flow | Gallons Pumped | Actual Flow Rate (gpm) | 00 Pond Stage (ft) | 00 Pond Elev (ft) Series 1 | 01 East Pond Flow Rate (gpm) | 01 East Total Flow | Gallons Pumped | Actual Flow Rate (gpm) | 01 East Pond Stage (ft) | 01E Pond Elev (ft) Series 1 | 01 West Total Flow | 01 West Pond Flow Rate (gpm) | Gallons Pumped | 01 West Total Flow (2nd Pump) | Gallons Pumped (2nd Pump) | Actual Flow Rate (gpm) | 01 West Pond Stage (feet) | 01W Pond Elev (ft) Series 1 | Notes | 26
[6 empty] | 5427.95 | [13 empty] | 5424.88
2021-01-06 | 13:00 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.52 | 5427.4
2021-01-13 | 9:40 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.54 | 5427.42
2021-01-20 | 12:00 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.54 | 5427.42
2021-01-27 | 13:30 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.54 | 5427.42
2021-02-03 | 14:30 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.56 | 5427.44
2021-02-10 | 13:00 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.54 | 5427.42
2021-02-17 | 12:15 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.52 | 5427.4
2021-02-24 | 13:30 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.58 | 5427.46
2021-03-03 | 14:00 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.58 | 5427.46
2021-03-10 | 15:30 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.6 | 5427.48
2021-03-17 | 14:30 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.58 | 5427.46
2021-03-24 | 15:00 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.52 | 5427.4
2021-03-31 | 11:00 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.52 | 5427.4
2021-04-07 | 14:00 |  |  |  |  | 0.96 | 5428.91 | [12 empty] | 2.52 | 5427.4
2021-04-14 | 12:00 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.64 | 5427.52
2021-04-21 | 9:15 |  |  |  |  | 1 | 5428.95 | [12 empty] | 2.55 | 5427.43
2021-04-28 | 9:45 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.55 | 5427.43
2021-05-05 | 10:00 |  |  |  |  | 0.95 | 5428.9 | [12 empty] | 2.55 | 5427.43
2021-05-12 | 12:10 |  |  |  |  | 1.05 | 5429 | [12 empty] | 2.55 | 5427.43
2021-05-19 | 13:00 |  |  |  |  | 1.05 | 5429 | [12 empty] | 2.55 | 5427.43
2021-05-26 | 12:00 |  |  |  |  | 1.05 | 5429 | [12 empty] | 2.55 | 5427.43
2021-06-02 | 11:30 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.58 | 5427.46
2021-06-09 | 11:00 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.58 | 5427.46
2021-06-16 | 10:30 |  |  |  |  | 1 | 5428.95 | [12 empty] | 2.56 | 5427.44
2021-06-23 | 13:30 |  |  |  |  | 0.98 | 5428.93 | [12 empty] | 2.6 | 5427.48
2021-06-30 | 11:00 |  |  |  |  | 0.95 | 5428.9 | [12 empty] | 2.58 | 5427.46

## W.Camp
Do Not Move, Add, or Remove any Columns After "Date" without Updating the Column Name Definitions - Do Not Remove the "Count" that the Definitions Reference --> | [8 empty] | Do Not Delete! | Do Not Delete!
Date | Time | Flow Rate (gpm) | Total Flow (gallons) | Average (gpm) | Elevation (ft.) | Comments | Count Chart Cells | 182
2020-12-31 | 7:20 | 186 | 544698750 | #VALUE! | 5421.36
2021-01-01 | 7:40 | 183 | 544965000 | 182.363 | 5421.34
2021-01-02 | 7:10 | 180 | 545224313 | 183.9099 | 5421.39
2021-01-03 | 9:00 | 187 | 545510250 | 184.4755 | 5421.37
2021-01-04 | 10:30 | 187 | 545787813 | 181.4137 | 5421.35
2021-01-05 | 10:30 | 159 | 546050563 | 182.4653 | 5421.31
2021-01-06 | 9:10 | 179 | 546284625 | 172.1044 | 5421.38
2021-01-07 | 10:45 | 160 | 546554188 | 175.6111 | 5421.4
2021-01-08 | 9:00 | 197 | 546787625 | 174.8592 | 5421.41
2021-01-09 | 7:45 | 199 | 547030063 | 177.6103 | 5421.42
2021-01-10 | 7:45 | 181 | 547285813 | 177.6042 | 5421.46
2021-01-11 | 9:00 | 186 | 547555313 | 177.8878 | 5421.46
2021-01-12 | 10:20 | 185 | 547827813 | 179.2763 | 5421.48
2021-01-13 | 9:30 | 175 | 548077563 | 179.6763 | 5421.47
2021-01-14 | 9:40 | 151 | 548331313 | 175 | 5421.39
2021-01-15 | 9:00 | 185 | 548574375 | 173.6157 | 5421.43
2021-01-16 | 7:45 | 185 | 548817313 | 177.9766 | 5421.4
2021-01-17 | 7:35 | 176 | 549069188 | 176.1364 | 5421.45
2021-01-18 | 8:35 | 195 | 549335875 | 177.7913 | 5421.39
2021-01-19 | 7:45 | 181 | 549577063 | 173.5165 | 5421.37
2021-01-20 | 9:05 | 195 | 549844500 | 175.9454 | 5421.43
2021-01-21 | 10:30 | 164 | 550114563 | 177.0905 | 5421.45
2021-01-22 | 9:30 | 189 | 550356250 | 175.1355 | 5421.44
2021-01-23 | 9:30 | 174 | 550610938 | 176.8667 | 5421.39
2021-01-24 | 14:00 | 180 | 550912280 | 176.2234 | 5421.46
2021-01-25 | 11:30 | 196 | 551140625 | 177.0116 | 5421.41
2021-01-26 | 10:15 | 157 | 551380375 | 175.641 | 5421.4
2021-01-27 | 9:30 | 178 | 551622625 | 173.6559 | 5421.45
2021-01-28 | 8:30 | 172 | 551863438 | 174.5022 | 5421.39
2021-01-29 | 9:00 | 194 | 552116313 | 172.0238 | 5421.39
2021-01-30 | 8:40 | 169 | 552361563 | 172.7113 | 5421.32
2021-01-31 | 9:20 | 169 | 552605500 | 164.8223 | 5421.41
2021-02-01 | 10:00 | 170 | 552852688 | 167.0189 | 5421.42
2021-02-02 | 10:00 | 163 | 553096313 | 169.184 | 5421.42
2021-02-03 | 9:25 | 170 | 553335938 | 170.5516 | 5421.48
2021-02-04 | 9:05 | 166 | 553575625 | 168.7937 | 5421.46
2021-02-05 | 9:40 | 165 | 553826875 | 170.339 | 5421.46
2021-02-06 | 7:20 | 165 | 554047375 | 169.6154 | 5421.45
2021-02-07 | 8:00 | 162 | 554301438 | 171.6642 | 5421.41
2021-02-08 | 10:25 | 172 | 554569750 | 169.282 | 5421.41
2021-02-09 | 10:30 | 170 | 554814313 | 169.2478 | 5421.42
2021-02-10 | 9:30 | 172 | 555044875 | 167.0739 | 5421.39
2021-02-11 | 11:00 | 152 | 555301125 | 167.4837 | 5421.4
2021-02-12 | 9:00 | 172 | 555522500 | 167.7083 | 5421.43
2021-02-13 | 8:55 | 168 | 555766813 | 170.253 | 5421.43
2021-02-14 | 9:40 | 157 | 556017250 | 168.6444 | 5421.4
2021-02-15 | 11:50 | 170 | 556284625 | 170.3025 | 5421.43
2021-02-16 | 12:35 | 163 | 556534188 | 168.0559 | 5421.38
2021-02-17 | 8:40 | 173 | 556733000 | 164.9892 | 5421.35
2021-02-18 | 8:30 | 156 | 556959750 | 158.5664 | 5421.39
2021-02-19 | 9:00 | 170 | 557197125 | 161.4796 | 5421.43
2021-02-20 | 12:35 | 169 | 557469188 | 164.3885 | 5421.39
2021-02-21 | 8:45 | 159 | 557665375 | 162.138 | 5421.4
2021-02-22 | 9:50 | 160 | 557909938 | 162.5003 | 5421.39
2021-02-23 | 10:00 | 168 | 558147625 | 163.9221 | 5421.4
2021-02-24 | 9:05 | 168 | 558374375 | 163.7184 | 5421.39
2021-02-25 | 8:45 | 171 | 558606000 | 163.1162 | 5421.5
2021-02-26 | 7:50 | 174 | 558841375 | 169.9458 | 5421.52
2021-02-27 | 7:45 | 163 | 559081625 | 167.4216 | 5421.49
2021-02-28 | 7:30 | 169 | 559315875 | 164.386 | 5421.45
2021-03-01 | 8:05 | 167 | 559558813 | 164.7037 | 5421.48
2021-03-02 | 9:10 | 171 | 559810625 | 167.3169 | 5421.49
2021-03-03 | 8:30 | 175 | 560046125 | 168.2143 | 5421.47
2021-03-04 | 8:25 | 165 | 560287188 | 167.9882 | 5421.45
2021-03-05 | 9:50 | 171 | 560529625 | 158.9751 | 5421.49
2021-03-06 | 8:25 | 191 | 560769188 | 176.7993 | 5421.54
2021-03-07 | 8:40 | 166 | 561016313 | 169.8454 | 5421.5
2021-03-08 | 9:25 | 169 | 561265938 | 168.0976 | 5421.51
2021-03-09 | 10:20 | 172 | 561523125 | 172.0314 | 5421.48
2021-03-10 | 7:30 | 175 | 561739063 | 170.0299 | 5421.53
2021-03-11 | 9:05 | 165 | 562002313 | 171.4984 | 5421.52
2021-03-12 | 8:30 | 177 | 562239563 | 168.8612 | 5421.51
2021-03-13 | 9:30 | 169 | 562492500 | 168.6247 | 5421.49
2021-03-14 | 6:15 | 162 | 562693938 | 161.7976 | 5421.52
2021-03-15 | 9:20 | 168 | 562973188 | 171.8462 | 5421.52
2021-03-16 | 10:30 | 170 | 563228875 | 169.3291 | 5421.49
2021-03-17 | 9:25 | 170 | 563459000 | 167.3636 | 5421.44
2021-03-18 | 9:00 | 165 | 563695313 | 167.0057 | 5421.45
2021-03-19 | 9:00 | 168 | 563935875 | 167.0569 | 5421.46
2021-03-20 | 8:20 | 168 | 564170750 | 167.7679 | 5421.48
2021-03-21 | 9:40 | 156 | 564424375 | 166.8586 | 5421.43
2021-03-22 | 9:00 | 169 | 564659063 | 167.6343 | 5421.49
2021-03-23 | 10:20 | 165 | 564912875 | 166.9816 | 5421.42
2021-03-24 | 7:40 | 169 | 565124438 | 165.2836 | 5421.48
2021-03-25 | 9:05 | 161 | 565385688 | 171.3115 | 5421.47
2021-03-26 | 7:10 | 166 | 565605438 | 165.8491 | 5421.44
2021-03-27 | 8:00 | 164 | 565852000 | 165.4779 | 5421.42
2021-03-28 | 8:10 | 162 | 566087813 | 162.6297 | 5421.43
2021-03-29 | 9:45 | 161 | 566347938 | 169.4625 | 5421.44
2021-03-30 | 10:45 | 163 | 566596063 | 165.4167 | 5421.43
2021-03-31 | 8:00 | 160 | 566802438 | 161.8627 | 5421.4
2021-04-01 | 10:40 | 168 | 567066188 | 164.8437 | 5421.45
2021-04-02 | 8:45 | 168 | 567289625 | 168.6317 | 5421.43
2021-04-03 | 9:00 | 167 | 567531188 | 166.0227 | 5421.43
2021-04-04 | 8:55 | 164 | 567769313 | 165.9408 | 5421.46
2021-04-05 | 10:20 | 168 | 568027563 | 169.3443 | 5421.46
2021-04-06 | 10:10 | 165 | 568266563 | 167.1329 | 5421.44
2021-04-07 | 8:45 | 165 | 568490000 | 164.8982 | 5421.43
2021-04-08 | 6:55 | 170 | 568713563 | 168.0925 | 5421.45
2021-04-09 | 9:15 | 161 | 568974188 | 164.9525 | 5421.43
2021-04-10 | 7:20 | 170 | 569194875 | 166.5562 | 5421.49
2021-04-11 | 7:15 | 161 | 569432938 | 165.8976 | 5421.43
2021-04-12 | 11:20 | 160 | 569708688 | 163.6499 | 5421.41
2021-04-13 | 8:45 | 166 | 569918813 | 163.5214 | 5421.4
2021-04-14 | 9:15 | 166 | 570159563 | 163.7755 | 5421.44
2021-04-15 | 8:20 | 162 | 570389625 | 166.1097 | 5421.44
2021-04-16 | 9:15 | 165 | 570634188 | 163.5873 | 5421.4
2021-04-17 | 10:00 | 159 | 570876938 | 163.468 | 5421.42
2021-04-18 | 9:05 | 166 | 571104250 | 164.1242 | 5421.43
2021-04-19 | 9:15 | 161 | 571340313 | 162.8021 | 5421.4
2021-04-20 | 8:45 | 159 | 571572188 | 164.4504 | 5421.41
2021-04-21 | 9:15 | 164 | 571811813 | 163.0102 | 5421.4
2021-04-22 | 8:30 | 170 | 572044313 | 166.6667 | 5421.45
2021-04-23 | 8:25 | 163 | 572281063 | 164.9826 | 5421.42
2021-04-24 | 8:10 | 163 | 572514938 | 164.1228 | 5421.42
2021-04-25 | 7:30 | 166 | 572746375 | 165.3121 | 5421.43
2021-04-26 | 10:10 | 161 | 573008188 | 163.6331 | 5421.39
2021-04-27 | 8:55 | 159 | 573226250 | 159.7524 | 5421.35
2021-04-28 | 8:55 | 159 | 573453813 | 158.0299 | 5421.33
2021-04-29 | 9:05 | 158 | 573681313 | 156.8966 | 5421.33
2021-04-30 | 10:15 | 163 | 573920438 | 158.3609 | 5421.41
2021-05-01 | 7:10 | 163 | 574123313 | 161.6534 | 5421.37
2021-05-02 | 7:00 | 155 | 574354063 | 161.3636 | 5421.38
2021-05-03 | 8:20 | 159 | 574594063 | 157.8947 | 5421.37
2021-05-04 | 9:55 | 156 | 574837313 | 158.4691 | 5421.36
2021-05-05 | 9:00 | 158 | 575053938 | 156.4079 | 5421.33
2021-05-06 | 9:15 | 162 | 575281250 | 156.2282 | 5421.36
2021-05-07 | 12:15 | 161 | 575541500 | 160.6481 | 5421.39
2021-05-08 | 11:15 | 154 | 575757563 | 156.5674 | 5421.34
2021-05-09 | 7:40 | 153 | 575947688 | 155.2041 | 5421.34
2021-05-10 | 7:26 | 154 | 576169875 | 155.8114 | 5421.34
2021-05-11 | 8:30 | 151 | 576395750 | 150.1828 | 5421.33
2021-05-12 | 12:10 | 155 | 576660875 | 159.7139 | 5421.35
2021-05-13 | 11:10 | 154 | 576875625 | 155.6159 | 5421.35
2021-05-14 | 8:20 | 156 | 577075125 | 157.0866 | 5421.37
2021-05-15 | 8:30 | 158 | 577302563 | 156.8538 | 5421.35
2021-05-16 | 8:55 | 158 | 577529875 | 155.1618 | 5421.36
2021-05-17 | 9:20 | 158 | 577760125 | 157.1672 | 5421.37
2021-05-18 | 8:40 | 160 | 577978938 | 156.295 | 5421.39
2021-05-19 | 8:00 | 152 | 578193938 | 153.5714 | 5421.35
2021-05-20 | 8:35 | 159 | 578424313 | 156.1864 | 5421.38
2021-05-21 | 10:05 | 148 | 578659313 | 153.5948 | 5421.35
2021-05-22 | 9:20 | 155 | 578870625 | 151.4781 | 5421.37
2021-05-23 | 8:30 | 168 | 579087813 | 156.2504 | 5421.39
2021-05-24 | 9:40 | 157 | 579325375 | 157.3258 | 5421.4
2021-05-25 | 8:20 | 156 | 579536688 | 155.3772 | 5421.35
2021-05-26 | 8:00 | 156 | 579758188 | 155.9859 | 5421.4
2021-05-27 | 8:15 | 160 | 579983563 | 154.8969 | 5421.4
2021-05-28 | 9:00 | 157 | 580218688 | 158.3333 | 5421.39
2021-05-29 | 7:10 | 154 | 580424375 | 154.6519 | 5421.35
2021-05-30 | 6:55 | 149 | 580646688 | 156.0091 | 5421.38
2021-05-31 | 7:00 | 158 | 580872938 | 156.5744 | 5421.37
2021-06-01 | 8:30 | 153 | 581113563 | 157.2712 | 5421.42
2021-06-02 | 8:05 | 159 | 581338500 | 158.9661 | 5421.41
2021-06-03 | 9:20 | 160 | 581580188 | 159.53 | 5421.43
2021-06-04 | 7:40 | 164 | 581795875 | 160.9604 | 5421.39
2021-06-05 | 10:15 | 161 | 582056375 | 163.3229 | 5421.41
2021-06-06 | 9:15 | 161 | 582279188 | 161.4587 | 5421.33
2021-06-07 | 8:55 | 156 | 582507875 | 161.0472 | 5421.34
2021-06-08 | 7:45 | 161 | 582724500 | 158.1204 | 5421.33
2021-06-09 | 9:45 | 157 | 582970688 | 157.8128 | 5421.34
2021-06-10 | 7:10 | 156 | 583175250 | 159.1922 | 5421.36
2021-06-11 | 8:15 | 144 | 583399750 | 149.1694 | 5421.36
2021-06-12 | 7:00 | 149 | 583608250 | 152.7473 | 5421.41
2021-06-13 | 12:00 | 157 | 583875625 | 153.6638 | 5421.44
2021-06-14 | 8:40 | 156 | 584064188 | 152.0669 | 5421.44
2021-06-15 | 9:15 | 157 | 584300250 | 160.042 | 5421.45
2021-06-16 | 8:30 | 150 | 584515313 | 154.167 | 5421.4
2021-06-17 | 6:45 | 152 | 584721063 | 154.1199 | 5421.42
2021-06-18 | 7:30 | 153 | 584952688 | 155.9764 | 5421.4
2021-06-19 | 8:40 | 150 | 585189250 | 156.6636 | 5421.45
2021-06-20 | 7:25 | 127 | 585383063 | 141.9875 | 5421.56
2021-06-21 | 12:20 | 154 | 585617875 | 135.3383 | 5421.74
2021-06-22 | 8:45 | 161 | 585815125 | 161.0204 | 5421.63
2021-06-23 | 11:50 | 155 | 586076563 | 160.8849 | 5421.59
2021-06-24 | 14:00 | 156 | 586321063 | 155.7325 | 5421.59
2021-06-25 | 9:00 | 155 | 586501125 | 157.9491 | 5421.47
2021-06-26 | 6:20 | 151 | 586696875 | 152.9297 | 5421.54
2021-06-27 | 6:15 | 152 | 586917188 | 153.5282 | 5421.56
2021-06-28 | 8:40 | 154 | 587165000 | 156.3483 | 5421.57
2021-06-29 | 9:05 | 157 | 587395125 | 157.0819 | 5421.6
2021-06-30 | 11:25 | 160 | 587646188 | 158.9006 | 5421.63

## DailyLog
Date | Time | Operator(s)/Staff | Temp | Weather | Operations | Contractor Work | Observations/Field Issues | Inspection Follow-Ups | Visitors to Site | Safety Topics/Meetings/Pre-Entries
2021-01-01 | 7:40 | Rob Neff | 18 to 34F | Partly cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Holiday weekend check
2021-01-02 | 7:10 | Kaleb Ferriter | 25 to 36F | Mostly Cloudy | Daily site checks, Daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | working alone-communication
2021-01-03 | 9:00 | Kaleb Ferriter | 16 to 39F | Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Working alione-communication
2021-01-04 | 10:30 | Taylor Stanich | 28 to 37F | Mostly cloudy | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, close out emms taskss |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Weekly sampling review sds for HN03
2021-01-05 | 10:30 | Taylor Stanich,Kaleb Ferriter | 12 to 36F | Mostly Sunny | Daily site checks, Daily parameters, waterfowl survey, WCP and IPS site/generator checks, |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Slips trips and falls
2021-01-06 | 9:10 | Taylor Stanich | 20 to 34F | Partly cloudy | Daily site checks, Daily parameters, BRW staff gauge monitoring, waterfowl survey, maintain freeway wetlands, clean CASB and ASB |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | social distancing
2021-01-07 | 10:45 | Taylor Stanich, Kaleb Ferriter | 14 to 34F | Overcast/Snow showers | Daily site checks, Daily parameters, Waterfowl survey, weekly sampling, monthly fire extinguisher checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Monthly fire extinguishers
2021-01-08 | 9:00 | Taylor Stanich | 15 to 35F | Clear, sunny | Daily site checks, Daily parameters, waterfowl survey, update ID locations, weekly epa summary report |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | eye protections
2021-01-09 | 7:45 | Taylor Stanich | 20F | Clear, sunny | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | working alone-communication
2021-01-10 | 7:45 | Taylor Stanich | 8F | Clear, sunny | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | working alone-communication
2021-01-11 | 9:00 | Taylor Stanich | 7 to 36F | Partly cloudy | Daily site checks, Daily parameters, waterfowl survey, MSD site/gen inspections, monthly compliance sampling, close out emms tasks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Monthly sampling-review sds for HNo3 and H2S04
2021-01-12 | 10:20 | Taylor Stanich, Kaleb Ferriter | 30 to 39F | Partly Cloudy | Daily site checks, daily parameters, WCP and IPS site/generator checks, waterfowl survey, tare/calibrate lime feeder |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Review sop for lime feeder tear/calibration
2021-01-13 | 9:30 | Taylor Stanich | 40 to 37F | Partly cloudy, windy | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, Monthly operations meeting, |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | High wind warning
2021-01-14 | 9:40 | Taylor Stanich | 11 to 32F | Mostly Sunny | Daily site checks, Daily parameters, Waterfowl survey, weekly sampling, weekly EPA summary report, clean lime silo |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Review SOP for Lime silo cleaning
2021-01-15 | 9:00 | Kaleb Ferriter | 10 to 35F | Partly Cloudy | Daily site checks, daily parameters, waterfowl survey |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | working alone-communication
2021-01-16 | 7:45 | Rob Neff | 16 to 39F | Partly cloudy | Daily site checks, Daily parameters, Weekend checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Working alone-communication
2021-01-17 | 7:35 | Rob Neff | 19 to 37F | Partly cloudy | Daily site checks, Daily parameters, Weekend checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Working alone-communication
2021-01-18 | 8:35 | Taylor Stanich | 25 to 32F | Overcast/Snow showers | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, MSD site/generator checks, MSD subdrain downloads, close out emms tasks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Slips trips and falls
2021-01-19 | 7:45 | Taylor Stanich, Kaleb Ferriter | 25 to 34F | Moslty sunny | Daily site checks, daily parameters, WCP and IPS site/generator checks, waterfowl survey, tare/calibrate lime feeder |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Review SOP for MSD subdrain sampling
2021-01-20 | 9:05 | Taylor Stanich | 17 to 38F | Partly cloudy | Daily site checks, Daily parameters, BRW staff guage monitoring, waterfowl survey, ship MSD samples, upload equis form |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | social distancing
2021-01-21 | 10:30 | Taylor Stanich | 20 to 36F | Overcast | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, weekly epa summary report, |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Weekly sampling review sds for HN03
2021-01-22 | 9:30 | Taylor Stanich, Kaleb Ferriter | 10 to 34F | Cloudy | Daily site checks, daily parameters, check screw conveyor bolts, waterfowl survey, upload equis collect forms, clean distrabution tank |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Snow and Ice
2021-01-23 | 9:30 | Jesse Sims | 3 to 28 F | Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | working alone-communication
2021-01-24 | 14:00 | Jesse Sims | 9 to 30 F | Partly Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | working alone-communication
2021-01-25 | 11:30 | Taylor Stanich | 7 to 34F | Mostly Sunny | Daily site checks, Daily parameters, waterfowl survey, MSD site/gen inspections, upload equis collect forms, close out emms tasks |  | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh |  | Cooler temps-proper clothing
2021-01-26 | 10:30 | Taylor Stanich, Kaleb Ferriter | 2 to 27F | Sunny | Daily site checks, Daily parameters, waterfowl survey, WCP and IPS site/generator checks, upload equis forms, effluent line camera inspection | Hunter Brothers-effluent camera inspection | Operating dry vault pumps, north and south lines. | CO2 @ 5cfh turned OFF @ 10:00 for Camera inspection |  | review tra for effluent camera inspection
2021-01-27 | 9:30 | Taylor Stanich | 2 to 32F | Mostly cloudy | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, upload Equis collect forms, remove MSD flow modules from mh106 and mh108 |  | Operating dry vault pumps, north and south lines. | CO2 Turned ON @ 13:00 to 10Cfh |  | Sanitation
2021-01-28 | 8:30 | Taylor Stanich | 16 to 39F | Partly cloudy | Daily site checks, Daily parameters, waterfowl survey, weekly sampling, Weekly EPA summary report, upload equis collect forms, MSD jetting | Hunter Bros/JCI MSD jetting | Operating dry vault pumps, north and south lines. | C02 @ 10 cfh increased to 15cfh @ 14:00 |  | Review SOP for MSD jetting
2021-01-29 | 9:00 | Taylor Stanich, Kaleb Ferriter | 18 to 37F | Cloudy | Daily site checks, daily parameters, switch MSD flow back to hcc, waterfowl survey, equis collect forms |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | proper mask wearing
2021-01-30 | 8:40 | Steve Lubick | 12 to 37 F | Snow showers | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | working alone-communication
2021-01-31 | 9:20 | Steve Lubick | 2 to 36 F | Clear calm | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. ASB pump not working upon arrival. | CO2 @ 15 cfh |  | working alone-communication
2021-02-01 | 10:00 | Taylor Stanich | 7 to 43F | Moslty sunny | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, MSD site/gen checks, close out emms tasks, uplaod equis collect forms, |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | Weekly sampling review sds for HN03
2021-02-02 | 10:00 | Taylor Stanich, Kaleb Ferriter | 19 to 46F | partly cloudy | daily site checks, daily parameters, waterfowl survey, inspect screw conveyor bolts, installed flow meters in subdrain, west camp site inspection, ips site inspection |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | review tra for subdrain flow meter installation
2021-02-03 | 9:25 | Taylor Stanich | 11 to 32F | Overcast | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, site snow removal, upload equis collect form, maintain freeway wetlands |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | Snow and Ice
2021-02-04 | 9:05 | Taylor Stanich | 18 to 32F | Overcast | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, weekly epa summary report, upload equis collect form |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | Continuing social distancing
2021-02-05 | 9:40 | Taylor Stanich, Kaleb Ferriter | 19 to 32F | Snow showers | Daily site checks, daily parameters, snow removal, waterfowl survey |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | Icy roads
2021-02-06 | 7:20 | Kaleb Ferriter | 10 to 30F | Snow showers | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | working alone-communication
2021-02-07 | 8:00 | Kaleb Ferriter | 10 to 30F | Snow showers | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | working alone-communication
2021-02-08 | 10:25 | Taylor Stanich | 7 to 22F | Snow showers | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, MSD site/gen checks, site snow removal, upload equis forms, | JCI lime delivery/snow removal | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | Snow removal
2021-02-09 | 10:30 | Taylor Stanich, Kaleb Ferriter | -8 to 21F | Cloudy | Daily site checks, daily parameters, WCP and IPS site/generator checks, waterfowl survey, upload equis collect forms, update ID locations |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | cold weather conditions
2021-02-10 | 9:30 | Taylor Stanich | -6 to 15F | Clear, cold | Daily site checks, Daily parameters, waterfowl survey, Montly operations meeting, BRW staff gauge monitoring, 1Q inspections, upload equis collect forms |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | heart dissease
2021-02-11 | 11:00 | Taylor Stanich | -11 to 1F | Overcast, scattered snow | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, weekly epa summary report, upload equis collect form |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh, reduced to 10 cfh |  | Wind chill warning
2021-02-12 | 9:00 | Taylor Stanich, Kaleb Ferriter | -18 to -2F | light snow showers | Daily site checks, daily parameters, oil change in wsp truck |  | Operating dry vault pumps, north and south lines. | CO2 @ 15 cfh |  | Freezing weather conditions
2021-02-13 | 8:55 | Taylor Stanich | -11 to 1F | Overcast, scattered snow | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | working alone-communication
2021-02-14 | 9:30 | Taylor Stanich | -6 to 15F | Clear, cold | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. Feeder/screw conveyor shut off, restarted @ 9:20 | CO2 @ 10 cfh |  | working alone-communication
2021-02-15 | 10:05 | Taylor Stanich | -11 to 1F | Overcast, scattered snow | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, MSD site/gen checks, upload equis collect form, inspect screw conveyor bolts |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Weekly sampling review sds for HN03
2021-02-16 | 12:35 | Taylor Stanich, Kaleb Ferriter | 23 to 30F | Overcast, scattered snow | Daily site checks, Daily parameters, waterfowl survey, WCP and IPS site/generator checks, upload quis collect forms, Install staff guages in HCC | Joe Mullaney- win 911 trouble shooting. JCI Lime delivery | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Slips trips and falls
2021-02-17 | 8:40 | Taylor Stanich | 15 to 27F | Overcast, scattered snow | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, upload Equis collect, 1Q inspecitons |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | social distancing
2021-02-18 | 8:30 | Taylor Stanich | 12 to 27F | Partly Cloudy | Daily site checks, Daily parameters, waterfowl survey, weekly sampling, weekly epa summary report, 1Q inspections, upload equis forms, monthly fire extinguishers |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh, CO2 turned off at 1300 |  | eye protection
2021-02-19 | 9:00 | Kaleb Ferriter | 12 to 34F | Mostly Cloudy | Daily site checks, daily parameters, waterfowl survey |  | Operating dry vault pumps, north and south lines. | CO2 OFF |  | Working alone-communication
2021-02-20 | 12:35 | Jesse Sims | 12 to 32F | Mostly Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ OFF |  | Working alone-communication
2021-02-21 | 8:45 | Jesse Sims | 30 to 34F | Mostly Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 OFF |  | Working alone-communication
2021-02-22 | 9:50 | Taylor Stanich | 34 to 42F | Partly cloudy | Daily site checks, Daily parameters, Monthly compliance sampling, Backflush asb pump, waterfowl survey, MSD site/gen checks, upload equis forms, close out emms tasks |  | Operating dry vault pumps, north and south lines. | CO2 turned on to 10 cfh @ 10:00 |  | Monthly sampling-review sds for HNo3 and H2S04
2021-02-23 | 10:00 | Taylor Stanich, Kaleb Ferriter | 14 to 33F | Mostly cloudy | Daily site checks, daily parameters, upload equis, waterfowl survey, bring truck to pro repair, 1Q inspections, WCP and IPS site/generator inspections |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | winter weather advisory
2021-02-24 | 9:05 | Taylor Stanich | 12 to 28F | Parly cloudy | Daily site checks, Daily parameters, BRW staff gauge monitoring, waterfowl survey, upload equis forms, 1Q inspections |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Ear/hearing protection
2021-02-25 | 8:45 | Taylor Stanich | 0 to 26F | Overcast | Daily site checks, Daily parameters, weekly report, waterfowl survey, weekly sampling, upload equis form, plc programming intro webinar |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | cold weather conditions
2021-02-26 | 7:50 | Taylor Stanich, Kaleb Ferriter | 25 to 30F | Overcast, scattered snow | Daily site checks, Daily parameters, waterfowl survey, upload equis collect forms, MSD subdrain downloads, SBC staff gauge readings |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Sanitation
2021-02-27 | 7:45 | Rob Neff | 1 to 27F | Partly cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Working alone-communication
2021-02-28 | 7:30 | Rob Neff | 4 to 31F | Partly cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Working alone-communication
2021-03-01 | 8:05 | Taylor Stanich | 11 to 37F | Mostly Sunny | Daily site checks, Daily parameters, weekly samling, waterfowl survey, MSD site/gen checks, upload equis form, MSD pigging | JCI MSD piggigng setup | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Changing weather conditions
2021-03-02 | 9:10 | Taylor Stanich, Kaleb Ferriter | 18 to 45F | Cloudy | Daily site checks, daily parameters, waterfowl survey, WCP site/gen inspection, IPS site/gen inspection, upload equis forms, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | hard hats
2021-03-03 | 8:30 | Taylor Stanich | 20 to 48F | Moslty sunny | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, upload equis, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Slips trips and falls
2021-03-04 | 8:25 | Taylor Stanich | 15 to 51F | Clear, sunny | Daily site checks, Daily parameters, waterfowl survey, Weekly sampling, weekly epa summary report, upload equis form, trouble shoot MSD communication loss | Joe Mullaney- MSD com loss trouble shooting | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Weekly sampling review sds for HN03
2021-03-05 | 8:50 | Taylor Stanich | 20 to 51F | Moslty sunny | Daily site checks, Daily parameters, waterfowl survey, NST pump test meeting, inspect screw conveyor bolts, upload equis form, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Biological hazards
2021-03-06 | 8:25 | Steve Lubick | 19 to 45 F | Overcast | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Working alone-communication
2021-03-07 | 8:40 | Steve Lubick | 22 to 43 F | Partly cloudy calm | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Working alone-communication
2021-03-08 | 9:25 | Taylor Stanich | 18 to 38F | Overcast | Daily site checks, Daily parameters, weekly sampling, MSD site/gen checks, upload quis data, waterfowl survey, | Joe Mullaney-MSD com loss trouble shooting | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | winter weather advisory
2021-03-09 | 10:20 | Taylor Stanich, Kaleb Ferriter | 21 to 39F | Moslty cloudy | Daily site checks, daily parameters, waterfowl survey, WCP/IPS site and gen checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | slick roads and dikes
2021-03-10 | 7:30 | Taylor Stanich | 15 to 36F | Parly cloudy | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, MSD subdrain sampling, upload equis data |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Review SOP for MSD subdrain sampling
2021-03-11 | 9:05 | Taylor Stanich | 10 to 40F | Mostly Sunny | Daily site checks, Daily parameters, waterfowl survey, weekly compliance sampling, upload equis data |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Muddy dike roads-drive with caution
2021-03-12 | 8:30 | Taylor Stanich, Kaleb Ferriter | 12 to 39F | Sunny | daily site checks, daily parameters, waterfowl survey |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | eye protection
2021-03-13 | 9:30 | Jesse Sims | 18 to 45F | Sunny | Daily site checks, Daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | working alone-communication
2021-03-14 | 6:15 | Jesse Sims | 20 to 51F | Sunny | Daily site checks, Daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | working alone-communication
2021-03-15 | 9:20 | Taylor Stanich | 23 to 48F | Partly cloudy | Daily site checks, Daily parameters, weekly sampling, MSD site/gen checks, upload quis data, waterfowl survey, | JCI lime delivery | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Weekly sampling review sds for HN03
2021-03-16 | 10:30 | Taylor Stanich, Kaleb Ferriter | 21 to 45F | Sunny | Daily site checks, daily parameters, WCP and IPS site/generator checks, upload equis data, 1Q pond level transducer verification, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Sanitation
2021-03-17 | 9:25 | Taylor Stanich | 23 to 48F | Clear, sunny | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, upload equis, annual site crane inspection |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Biological hazards
2021-03-18 | 9:00 | Taylor Stanich | 20 to 51F | Clear, sunny | Daily site checks, Daily parameters, Weekly compliance sampling, waterfowl survey, Weekly epa summary report Distrabution tank maintenance, Monthly C02 tank inspection |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Continuing social distancing
2021-03-19 | 9:00 | Taylor Stanich, Kaleb Ferriter | 27 to 48F | Cloudy | Daily site checks, daily parameters, waterfowl survey, installed C8.5 trib flow meter, update sample forms, upload equis form |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Muddy dike roads-drive with caution
2021-03-20 | 8:20 | Taylor Stanich | 19 to 37F | Partly cloudy | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | working alone-communication
2021-03-21 | 9:40 | Taylor Stanich | 23 to 40F | Overcast | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | working alone-communication
2021-03-22 | 9:00 | Taylor Stanich | 32 to 48F | Overcast | Daily site checks, Daily parameters, Monthly compliance sampling, Backflush asb pump, waterfowl survey, MSD site/gen checks, upload equis forms, close out emms tasks |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Monthly sampling-review sds for HNo3 and H2S04
2021-03-23 | 10:20 | Taylor Stanich, Kaleb Ferriter | 18 to 37F | Partly Cloudy | Daily site checks, daily parameters, WCP and IPS site/generator checks, upload equis forms, gather materials/equip needed for msd subdrain |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Slips trips and falls
2021-03-24 | 7:40 | Taylor Stanich, Rob Neff | 23 to 39F | Overcast | Daily site checks, Daily parameters, BRW staff gauge monitoring, waterfowl survey, upload equis form, Sample MSD subdrains |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | MSD subdrains, Review SOP
2021-03-25 | 9:05 | Taylor Stanich | 30 to 37F | Mostly cloudy | Daily site checks. Daily parameters, weekly sampling, waterfowl survey, clean lime silo, weekly epa summary report, upload equis form, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Sanitation
2021-03-26 | 7:00 | Steve Lubick, Rob Neff | 27 to 39 F | Mostly cloudy | Daily site checks. Daily parameters, weekly sampling, waterfowl survey, upload equis form, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Hard Hats
2021-03-27 | 8:00 | Kaleb Ferriter | 32 to 50F | Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | working alone-communication
2021-03-28 | 8:10 | Kaleb Ferriter | 21 to 57F | Partly Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | working alone-communication
2021-03-29 | 9:45 | Taylor Stanich | 20 to 36F | Overcast, windy | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, MSD site/generator checks, close out emms tasks, upload equis, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | High wind warning
2021-03-30 | 10:45 | Taylor Stanich, Kaleb Ferriter | 15 to 32F | Mostly sunny, windy | Daily site checks, daily parameters, WCP and IPS site/generator checks, waterfowl survey, upload equis form, inspect screw conveyor bolts, grease screw conveyor, |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | melting snow and ice
2021-03-31 | 8:00 | Taylor Stanich | 20 to 44F | Clear, sunny | Daily site checks, Daily parameters, waterfowl survey, BRW staff guage monitoring, upload equis forms, silt curtain inspections, piping & structures inspection |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh |  | Biological hazards
2021-04-01 | 10:40 | Taylor Stanich | 22 to 51F | Clear, sunny | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, monthly group meeting, install equipment blank tubing in eff sample line, upload equis, weekly epa summary report |  | Operating dry vault pumps, north and south lines. | CO2 @ 10 cfh turned OFF @ 13:30 |  | Weekly sampling review sds for HN03
2021-04-02 | 8:45 | Taylor Stanich, Kaleb Ferriter | 34 to 63F | Clear, Sunny | Daily site checks, daily parameters, waterfowl survey, upload equis collect forms, clean c channel |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Review SOP for channel cleaning
2021-04-03 | 9:00 | Steve Lubick | 34 to 63 F | Clear, Sunny | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-04-04 | 8:55 | Steve Lubick | 32 to 62 F | Partly cloudy calm | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-04-05 | 10:20 | Taylor Stanich | 29 to 36F | Overcast, snow showers | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, upload equis form, MSD site/gen checks, close out emms tasks | JCI dredge set-up | Operating dry vault pumps, north and south lines. | C02 OFF |  | Weekly sampling review sds for HN03
2021-04-06 | 10:10 | Taylor Stanich, Kaleb Ferriter | 23 to 52F | Sunny | Daily site checks, Daily parameters, cleaned channels, WCP/IPS site checks, dredge set up, upload equis form, waterfowl survey | JCI dredge set-up | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hand protection
2021-04-07 | 8:45 | Taylor Stanich | 22 to 53F | Sunny | Daily site checks, Daily parameters, waterfowl survey, BRW staff gauge monitoring, dredge ops oversight, | JCI dredge set-up/started dredging A1 @ 10:00 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Pinch points
2021-04-08 | 6:55 | Taylor Stanich, Rob Neff | 18 to 36F | Overcast | Daily site checks, Daily parameters, waterfowl survey, weekly sampling, | JCI dredging A1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Proper PPE
2021-04-09 | 9:15 | Taylor Stanich | 17 to 45F | Mostly sunny | Daily site checks, Daily parameters, waterfowl survey, decant water from north drying bed, upload equis |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Biological hazards
2021-04-10 | 7:20 | Rob Neff | 19 to 46F | Partly cloudy | Daily site checks, daily parameters,upload equis form |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-04-11 | 7:15 | Rob Neff | 16 to 37F | Partly cloudy | Daily site checks, daily parameters,upload equis form |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-04-12 | 11:20 | Taylor Stanich | 24 to 37F | Overcast | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, close out emms taskss, | JCI dredging A1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Weekly sampling review sds for HN03
2021-04-13 | 8:45 | Taylor Stanich, Kaleb Ferriter | 18 to 36F | Partly Cloudy | Daily site checks, Daily parameters, waterfowl survey, upoad equis, Monthly eyewash/fire extinguisher checks, WCP and IPS site/gen checks | JCI dredging A1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Monthly fire extinguishers
2021-04-14 | 9:15 | Taylor Stanich | 20 to 35F | Overcast | Daily site checks, Daily parameters, BRW staff gauge monitoring, Monitor dredge operations, waterfowl survey, upoad equis | JCI dredging A1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Aggressive geese nesting on dikes
2021-04-15 | 8:20 | Taylor Stanich | 32 to 42F | Overcast | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, weekly epa summary report, upload equis collect form, IPS pump 1 maintenance | JCI dredging A1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hand protection
2021-04-16 | 9:15 | Taylor Stanich, Kaleb Ferriter | 21 to 46F | Mostly Sunny | Daily site checks, daily parameters, Pump 1 maintenance, upload equis form, water fowl survey, Decant water from north drying bed |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hi Po incident
2021-04-17 | 10:00 | Kaleb Ferriter | 28 to 57F | Sunny | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-04-18 | 9:05 | Kaleb Ferriter | 27 to 55F | Sunny | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-04-19 | 9:15 | Taylor Stanich, Kaleb Ferriter | 12 to 34F | Snow showers | Daily site checks, daily parameters, waterfowl survey, Monthly compliance sampling, MSD site/gen checks, upload equis, monitor dredge ops | JCI dredging B1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Monthly sampling-review sds for HNo3 and H2S04
2021-04-20 | 8:25 | Taylor Stanich, Kaleb Ferriter | 16 to 39F | Sunny | Daily site checks, daily parameters, WCP/IPS site and gen inspection, upload equis, clean A channel | JCI dredging B1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hand tool safety
2021-04-21 | 9:15 | Taylor Stanich, Kaleb Ferriter | 21 to 48F | Sunny | Daily site checks, daily parameters, BRW staff gauge monitoring, waterfowl survey, upload equis, inspect screw conveyor bolts, finish cleaning a channel | JCI dredging B1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | eye protection
2021-04-22 | 8:30 | Taylor Stanich | 30 to 44F | Overcast | Daily site checks, Daily parameters, weekly sampling, weekly epa summary report, waterfowl survey, msd channel sediment sampling | JCI dredging B1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Review SOP s-03 for sediment sampling
2021-04-23 | 8:25 | Taylor Stanich | 25 to 48F | Overcast | Daily site checks, Daily parameters, waterfowl survey, upload equis, decant water from north drying bed |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Slips trips and falls
2021-04-24 | 8:10 | Taylor Stanich | 26 to 48F | Overcast | Daily site checks, Daily parameters, Weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-04-25 | 7:30 | Taylor Stanich | 27 to 48F | Overcast rain | Daily site checks, Daily parameters, Weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-04-26 | 10:10 | Taylor Stanich, Kaleb Ferriter | 28 to 46F | Mostly Sunny | Daily site checks, daily parameters, MSD site/gen inspections, Weekly sampling, upload equis, Chipped A and C channel discharge, waterfowl survey | JCI dredging B1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Muddy dike roads-drive with caution
2021-04-27 | 9:00 | Taylor Stanich, Kaleb Ferriter | 21 to 55F | Sunny | Daily site checks, daily parameters, waterfowl survey, IPS and WCP site/generator checks, remove weed piles from IPS, Help JCI with dredge move to c | JCI dredging B1, moved to C1 @ 3:30 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Sanitation
2021-04-28 | 9:00 | Taylor Stanich, Kaleb Ferriter | 32 to 61F | Cloudy | Daily site checks, Daily parameters, BRW staff guage monitoring, waterfowl survey, upload equis form, MSD subdrain downloads | JCI dredging C1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hand protection
2021-04-29 | 9:05 | Taylor Stanich | 32 to 67F | Partly cloudy | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, upload equis, Weekly epa summary report, decant water from north drying bed, site building maintenance | JCI dredging C1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Weekly sampling review sds for HN03
2021-04-30 | 10:15 | Steve Lubick | 41 to 73 F | Partly cloudy calm | Daily site checks, Daily parameters, waterfowl survey, upload equis, decant water from north drying bed |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Sunscreen
2021-05-01 | 7:10 | Rob Neff | 36 to 64F | Partly cloudy | Daily site checks, Daily parameters, Upload equis, decant water from north drying bed |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-05-02 | 7:00 | Rob Neff | 27 to 48F | Partly cloudy | Daily site checks, Daily parameters, Upload equis, decant water from north drying bed |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-05-03 | 8:20 | Taylor Stanich | 25 to 54F | Moslty sunny | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, MSD site/generator checks, upload equis, close out emms tasks, | JCI dredging C1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Biological hazards
2021-05-04 | 9:55 | Kaleb Ferriter | 34 to 54F | Cloudy | Daily site checks, daily parameters, waterfowl survey, equis, decanting, wcp site and gen inspection, ips site and gen inspection | JCI dredging C1 | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-05-05 | 9:00 | Kaleb Ferriter | 32 to 60F | Sunny | Daily site checks, daily parameters, waterfowl survey, brw staff gauge monitoring, cleaned freeway wetlands, brought gmc to oreillys for check engine light, monthly fire extinguisher check | JCI dredging C1/Dredge demob | Operating dry vault pumps, north and south lines. | C02 OFF |  | eye protection
2021-05-06 | 9:15 | Steve Lubick | 28 to 72 F | Partly cloudy calm | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, upload equis. | JCI dredge demob | Operating dry vault pumps, north and south lines. | C02 OFF |  | Foot Protection
2021-05-07 | 12:15 | Kaleb Ferriter | 32 to 57F | Cloudy | Daily site checks, daily parameters, filled out MSD logbooks for subdrain sampling, decanting, equis upload |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-05-08 | 11:15 | Kaleb Ferriter | 28 to 41F | Cloudy, Windy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-05-09 | 7:40 | Kaleb Ferriter | 30 to 50F | Partly Cloudy | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-05-10 | 7:26 | Taylor Stanich, Steve Lubick | 33 to 53F | Partly cloudy | Daily site checks, Daily parameters, Monthly compliance sampling, Backflush asb pump, waterfowl survey, MSD site/gen checks, upload equis forms, close out emms tasks | JCI D4 dredging ops set up | Operating dry vault pumps, north and south lines. | C02 OFF |  | Monthly sampling-review sds for HNo3 and H2S04
2021-05-11 | 8:30 | Taylor Stanich, Kaleb Ferriter | 21 to 54F | Sunny | Daily site checks, daily parameters, waterfowl survey, IPS and WCP site/generator checks, MSD subdrain sampling, upload equis | JCI D4 dredging ops set up | Operating dry vault pumps, north and south lines. | C02 OFF |  | Review SOP for subdrain sampling
2021-05-12 | 12:10 | Taylor Stanich, Kaleb Ferriter | 27 to 61 | Sunny | Daily site checks, daily parameters, Monthly ops meeting, waterfowl survey, BRW staff gauge monitoring, Equis form corrections, | JCI D4 dredging ops set up | Operating dry vault pumps, north and south lines. | C02 OFF |  | Slips trips and falls
2021-05-13 | 11:10 | Taylor Stanich, Kaleb Ferriter | 30 to 63F | Partly Cloudy | Daily site checks, Daily parameters, Weekly sampling, waterfowl survey, dredge ops oversight, monthly group meeting, upload equis | JCI D4 dredging ops set up | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working aroung heavy equipment
2021-05-14 | 8:20 | Taylor Stanich | 33 to 64F | Partly cloudy | Daily site checks, Daily parameters, weekly epa summary report, waterfowl survey, upload historical equis data |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Changing weather conditions
2021-05-15 | 8:30 | Steve Lubick | 35 to 65 F | Clear calm | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-05-16 | 8:55 | Steve Lubick | 36 To 73 F | Clear calm | Daily site checks, daily parameters |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-05-17 | 9:20 | Taylor Stanich, Kaleb Ferriter | 36 to 77F | Sunny | Daily site checks, Daily parameters, weekly sampling, waterfowl survey, msd site/generator checks, monitor D4 dredging, monitor channel PH, started 2Q inspections | JCI started dredging D4 @ 9:00 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Pinch points
2021-05-18 | 8:40 | Taylor Stanich, Kaleb Ferriter | 39 to 68F | Sunny | Daily site checks, daily parameters. Waterfowl survey, WCP/IPS site and gen inspection, monitored dredging operations, monitored drying beds, monitored channel PH, 2Q inspection | JCI started dredging D4 @ 7:00 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hydration
2021-05-19 | 8:00 | Taylor Stanich, Kaleb Ferriter | 38 to 53F | Overcast | Daily site checks, Daily parameters, waterfowl survey, BRW staff guage monitoring, upload equis forms, Monitor D4 dredging, 2Q inspections | JCI dredging D4 | Operating dry vault pumps, north and south lines. | C02 OFF |  | winter weather advisory
2021-05-20 | 8:35 | Taylor Stanich, Kaleb Ferriter | 31 to 41F | Overcast, snow showers | Daily site checks, Daily parameters, weekly sampling, weekly epa summary report, waterfowl survey, | JCI dredging D4 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Snow showers
2021-05-21 | 10:05 | Taylor Stanich, Kaleb Ferriter | 23 to 36F | Overcast, snow showers | Daily site checks, daily parameters, decanting, | JCI dredging D4 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Slips trips and falls
2021-05-22 | 9:20 | Taylor Stanich | 27 to 37F | Partly cloudy | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-05-23 | 8:30 | Taylor Stanich | 23 to 40F | Overcast | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-05-24 | 9:40 | Taylor Stanich, Kaleb Ferriter | 39 to 52F | Overcast | Daily site checks, daily parameters. Waterfow survey, Weekly sampling, upload equis, decant water from north drying bed, MSD site/generator checks, air compressor #1 maintenance | JCI dredging D4 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Muddy roads
2021-05-25 | 8:20 | Taylor Stanich, Kaleb Ferriter | 36 to 57F | Mostly Sunny | Daily site checks, daily parameters, waterfowl survey, WCP and IPS site/generator checks, HCC weed removal, 2Q site inspections, CB8 and CB9 check, freeway wetlands check, | JCI dredging D4 | Operating dry vault pumps, north and south lines. | C02 @ 5CFH @ 10:00 |  | watch for baby geese on site
2021-05-26 | 8:50 | Taylor Stanich, Kaleb Ferriter | 36 to 48F | Mostly Cloudy | Daily site checks, daily parameters, waterfowl survey, BRW staff gauge monitoring, HCC weed removal, Air compressor #2 maintenance, | JCI dredging D4 | Operating dry vault pumps, north and south lines. | C02 5CFH |  | review sop for BRW Staff Gauge monitoring.
2021-05-27 | 8:15 | Taylor Stanich, Kaleb Ferriter | 35 to 65F | Clear sunny | Daily site checks, Daily parameters, waterfowl survey, weekly sampling, inspect screw conveyor bolts, weekly epa summary report | JCI dredging D4 | Operating dry vault pumps, north and south lines. | C02 @ 5CFH, increased to 10 CFH @ 1300 |  | Weekly sampling review sds for HN03
2021-05-28 | 9:00 | Kaleb Ferriter | 36 to 57F | Mostly Sunny | daily site checks, daily parameters, waterfowl survey, picked up motor oil from ACE, reduced lime rate |  | Operating dry vault pumps, north and south lines. | C02 10CFH |  | Working alone-communication
2021-05-29 | 7:10 | Rob Neff | 30 to 61F | Sunny | Daily site checks, Daily parameters, weekend checks, Upload equis, decant water from north drying bed |  | Operating dry vault pumps, north and south lines. | C02 10CFH |  | Working alone-communication
2021-05-30 | 6:55 | Rob Neff | 36 to 70F | Sunny | Daily site checks, Daily parameters, weekend checks, Upload equis, decant water from north drying bed and south drying bed, Move crane from north drying bed to south drying bed, |  | Operating dry vault pumps, north and south lines. | C02 10CFH |  | Working alone-communication
2021-05-31 | 7:00 | Rob Neff | 43 to 73F | Sunny | Daily site checks, Daily parameters, weekend checks, Upload equis, decant water from south drying bed, |  | Operating dry vault pumps, north and south lines. | C02 10CFH |  | Working alone-communication
2021-06-01 | 8:30 | Taylor Stanich | 40 to 77F | Clear, sunny | Daily site checks, Daily parameters, Weekly sampling, MSD, WCP, and IPS site/generator checks, waterfowl survey, decant water from south drying bed, Close out weekly emms tasks | JCI Dredging D4 | Operating dry vault pumps, north and south lines. | C02 OFF |  | Weekly sampling review sds for HN03
2021-06-02 | 8:05 | Taylor Stanich | 41 to 77F | Clear, sunny | Daily site checks, Daily parameters, waterfowl suvey, BRW staff guage monitoring, upload equis, clean site vehicles, clean ops building, clean distrabution tank/weir gates | JCI dredging D4, finished @ 14:00 started dredge demob | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hydration
2021-06-03 | 9:20 | Taylor Stanich | 48 to 86F | Clear, sunny | Daily site checks, Daily parameters, weekly sampling, weekly epa summary report, monthly c02 inspection, upload equis, fix D3 level transducer, help JCI with dredge demob | JCI dredge demob | Operating dry vault pumps, north and south lines. | C02 OFF |  | Biological hazards
2021-06-04 | 7:40 | Taylor Stanich | 48 to 82F | Mostly sunny | Daily site checks, Daily parameters, upload equis, D3 level transducer trouble shooting, decant water from south drying bed | JCI dredge demob | Operating dry vault pumps, north and south lines. | C02 OFF |  | Sun Exposure
2021-06-05 | 10:15 | Steve Lubick | 46 to 75 F | Partly cloudy | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-06-06 | 9:15 | Steve Lubick | 39 to 68 F | Partly cloudy breezy | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-06-07 | 8:55 | Taylor Stanich | 34 to 76F | Moslty sunny | Daily site checks, daily parameters, MSD site/gen inspections, Weekly sampling, upload equis, |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Weekly sampling review sds for HN03 and H2s04
2021-06-08 | 7:45 | Taylor Stanich | 38 to 70F | overcast | Daily site checks, Daily parameters, WCP and IPS site/generator checks, decant water from north drying bed, game camera checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Thunderstorms possible-30/30rule
2021-06-09 | 9:45 | Taylor Stanich | 40 to 76F | Clear, sunny | Daily site checks, Daily parameters, monthly operations meeting, decant water from north drying bed, Monthly fire extinguisher checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Monthly fire extinguishers
2021-06-10 | 7:10 | Taylor Stanich | 41 to 66F | Mostly cloudy | Daily site checks, Daily parameters, Weekly sampling, decant water from north drying bed, upload equis, install temperature probes @WSP |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | hard hats
2021-06-11 | 8:15 | Taylor Stanich | 32 to 64F | Mostly sunny | Daily site checks, Daily parameters, weekly epa summary report, upload historical equis data |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Tick season
2021-06-12 | 7:00 | Kaleb Ferriter | 39 to 73F | Overcast | Weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-06-13 | 12:00 | Kaleb Ferriter | 35 to 80F | Sunny | Weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-06-14 | 8:40 | Taylor Stanich, Kaleb Ferriter | 45 to 90F | Sunny | Daily site checks, daily parameters, monthly sampling, Removed MSD subdrain flow modules for jetting/pigging, MSD site/gen checks, close out emms tasks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Eye protection
2021-06-15 | 9:15 | Taylor Stanich | 51 to 88F | Clear, sunny | Daily site checks, Daily parameters, upload equis, monitor MSD vault level for jetting, WCP and IPS site/generator checks, clean flow meters/check desicant | Tw enterprises-generator maintenance, JCI MSD jetting | Operating dry vault pumps, north and south lines. | C02 OFF |  | Review SOP for MSD jetting
2021-06-16 | 8:30 | Taylor Stanich | 50 to 77F | Sunny | Daily site checks, daily parameters, BRW staff gauge readings, MSD jetting, monitor vault level for jetting, upload equis | JCI MSD jetting | Operating dry vault pumps, north and south lines. | C02 OFF |  | Warmer temps-stay hydrated
2021-06-17 | 6:45 | Taylor Stanich, Rob Neff | 40 to 78F | Sunny | Daily site checks, Daily parameters, Weekly sampling, upload equis, MSD pigging | JCI-MSD pigging | Operating dry vault pumps, north and south lines. | C02 OFF |  | Pinch points
2021-06-18 | 7:30 | Taylor Stanich, Kaleb Ferriter | 40 to 80F | Sunny | Daily site checks, daily parameters, decant water from north drying bed, Upload equis, upload msd flow data |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Driving Safety
2021-06-19 | 8:40 | Taylor Stanich | 56F | Moslty sunny | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-06-20 | 7:25 | Taylor Stanich | 58F | Partly cloudy | Daily site checks, Daily parameters, weekend checks |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-06-21 | 12:20 | Taylor Stanich, Kaleb Ferriter | 70F | Mostly Sunny | Daily site checks, daily parameters, reinstalled flow meters into MSD, MSD site and gen check, picked up pressure washer from parrot, weekly sampling, dropped samples off ar FedEx, Decant water from north drying bed |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | sun protection - long sleeves
2021-06-22 | 8:45 | Taylor Stanich, Kaleb Ferriter | 48 to 78F | Clear, sunny | Daily site checks, Daily parameters, WCP and IPS site/generator checks, started cleaning distrabution channels, super sacker dry run | JCI-Super sacker set-up | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hard Hats
2021-06-23 | 11:50 | Taylor Stanich, Kaleb Ferriter | 56 to 79F | Parly cloudy | Daily site checks, Daily parameters, BRW staff gauge monitoring, clean conveyance channels C and B, upload equis, |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Review TRA for conveyance channel cleaning
2021-06-24 | 14:00 | Taylor Stanich, Kaleb Ferriter | 50 to 79F | Mostly Sunny | Daily site checks, daily parameters, finished cleaning A and B channel, weekly sampling, equis upload, weekly epa summary report |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Eye protection
2021-06-25 | 9:00 | Kaleb Ferriter | 46 to 73F | Sunny | Daily site checks, daily parameters, equis corrections, equis uploads |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | working alone-communication
2021-06-26 | 6:20 | Rob Neff | 46 to 77F | Partly cloudy | Daily site checks, daily parameters, equis uploads |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-06-27 | 6:15 | Rob Neff | 48 to 81F | Sunny | Daily site checks, daily parameters, equis uploads |  | Operating dry vault pumps, north and south lines. | C02 OFF |  | Working alone-communication
2021-06-28 | 8:40 | Taylor Stanich, Kaleb Ferriter | 48 to 88F | Sunny | Daily site checks, daily parameters, equis uploads, weekly sampling, MSD site/generator checks, security camera installation help, pond/vegitation inspections | Colbert elec.-security camera installation | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hydration
2021-06-29 | 9:05 | Taylor Stanich | 53 to 91F | Clear, sunny | Daily site checks, Daily parameters, WCP and IPS site/generator checks, replace D3 level transducer, pond/vegetation inspections, freeway wetlands weed removal | Colbert elec.-security camera installation | Operating dry vault pumps, north and south lines. | C02 OFF |  | Very hot daytime temps- heat stress
2021-06-30 | 11:25 | Taylor Stanich, Kaleb Ferriter | 55 to 93F | Clear, sunny | Daily site checks, Daily parameters, BRW staff gauge monitoring, pond/veg/flood plain inspections, CB8 maintenance, upload equis | Colbert elec.-security camera installation | Operating dry vault pumps, north and south lines. | C02 OFF |  | Hand tool safety